## in
Spandrels R(ft2·°F·h/BTU) | Glass R(ft2·°F·h/BTU) | Air Leakage | LPD | ERV | Controls | HVAC System | TEUI kWh/m2 | TEDI kWh/m2 | GHGI kgCO2/m2 | En Saving % | GHG Saving%
5 | 2.8 | Current | Current | None | Current | Current | 216 | 101 | 39 | 0 | 0
5 | 2.8 | Current | Current | 75% | Current | Current | 183 | 66 | 33 | 15 | 16
5 | 2.8 | Current | 25% | None | Current | Current | 214 | 104 | 39 | 1 | 1
5 | 2.8 | Current | 25% | 75% | Current | Current | 181 | 68 | 32 | 16 | 17
5 | 2.8 | Improved | Current | None | Current | Current | 214 | 99 | 38 | 1 | 1
5 | 2.8 | Improved | Current | 75% | Current | Current | 181 | 64 | 32 | 16 | 17
5 | 2.8 | Improved | 25% | None | Current | Current | 212 | 102 | 38 | 2 | 2
5 | 2.8 | Improved | 25% | 75% | Current | Current | 179 | 66 | 32 | 17 | 18
5 | 4 | Current | Current | None | Current | Current | 209 | 93 | 37 | 3 | 4
5 | 4 | Current | Current | 75% | Current | Current | 175 | 58 | 31 | 19 | 20
5 | 4 | Current | 25% | None | Current | Current | 206 | 96 | 37 | 5 | 5
5 | 4 | Current | 25% | 75% | Current | Current | 173 | 60 | 31 | 20 | 21
5 | 4 | Improved | Current | None | Current | Current | 207 | 91 | 37 | 4 | 5
5 | 4 | Improved | Current | 75% | Current | Current | 174 | 56 | 31 | 20 | 21
5 | 4 | Improved | 25% | None | Current | Current | 204 | 94 | 37 | 5 | 5
5 | 4 | Improved | 25% | 75% | Current | Current | 171 | 58 | 30 | 21 | 22
5 | 5.5 | Current | Current | None | Current | Current | 205 | 89 | 37 | 5 | 5
5 | 5.5 | Current | Current | 75% | Current | Current | 172 | 54 | 30 | 21 | 22
5 | 5.5 | Current | 25% | None | Current | Current | 202 | 91 | 36 | 6 | 6
5 | 5.5 | Current | 25% | 75% | Current | Current | 169 | 56 | 30 | 22 | 23
5 | 5.5 | Improved | Current | None | Current | Current | 203 | 87 | 36 | 6 | 6
5 | 5.5 | Improved | Current | 75% | Current | Current | 170 | 52 | 30 | 21 | 23
5 | 5.5 | Improved | 25% | None | Current | Current | 201 | 89 | 36 | 7 | 7
5 | 5.5 | Improved | 25% | 75% | Current | Current | 167 | 54 | 30 | 22 | 24
10 | 2.8 | Current | Current | None | Current | Current | 211 | 95 | 38 | 2 | 3
10 | 2.8 | Current | Current | 75% | Current | Current | 178 | 60 | 32 | 18 | 19
10 | 2.8 | Current | 25% | None | Current | Current | 208 | 98 | 38 | 4 | 3
10 | 2.8 | Current | 25% | 75% | Current | Current | 175 | 63 | 31 | 19 | 20
10 | 2.8 | Improved | Current | None | Current | Current | 209 | 93 | 37 | 3 | 3
10 | 2.8 | Improved | Current | 75% | Current | Current | 176 | 58 | 31 | 19 | 20
10 | 2.8 | Improved | 25% | None | Current | Current | 206 | 96 | 37 | 4 | 4
10 | 2.8 | Improved | 25% | 75% | Current | Current | 174 | 61 | 31 | 20 | 21
10 | 4 | Current | Current | None | Current | Current | 203 | 87 | 36 | 6 | 6
10 | 4 | Current | Current | 75% | Current | Current | 170 | 52 | 30 | 21 | 23
10 | 4 | Current | 25% | None | Current | Current | 201 | 90 | 36 | 7 | 7
10 | 4 | Current | 25% | 75% | Current | Current | 168 | 54 | 30 | 22 | 24
10 | 4 | Improved | Current | None | Current | Current | 201 | 85 | 36 | 7 | 7
10 | 4 | Improved | Current | 75% | Current | Current | 168 | 50 | 30 | 22 | 24
10 | 4 | Improved | 25% | None | Current | Current | 199 | 88 | 36 | 8 | 8
10 | 4 | Improved | 25% | 75% | Current | Current | 166 | 52 | 29 | 23 | 25
10 | 5.5 | Current | Current | None | Current | Current | 200 | 83 | 36 | 8 | 8
10 | 5.5 | Current | Current | 75% | Current | Current | 166 | 48 | 29 | 23 | 25
10 | 5.5 | Current | 25% | None | Current | Current | 197 | 86 | 35 | 9 | 9
10 | 5.5 | Current | 25% | 75% | Current | Current | 164 | 50 | 29 | 24 | 25
10 | 5.5 | Improved | Current | None | Current | Current | 198 | 81 | 35 | 8 | 9
10 | 5.5 | Improved | Current | 75% | Current | Current | 164 | 46 | 29 | 24 | 26
10 | 5.5 | Improved | 25% | None | Current | Current | 195 | 84 | 35 | 10 | 10
10 | 5.5 | Improved | 25% | 75% | Current | Current | 162 | 48 | 29 | 25 | 26
15 | 2.8 | Current | Current | None | Current | Current | 209 | 93 | 38 | 3 | 3
15 | 2.8 | Current | Current | 75% | Current | Current | 176 | 58 | 31 | 19 | 20
15 | 2.8 | Current | 25% | None | Current | Current | 207 | 96 | 37 | 4 | 4
15 | 2.8 | Current | 25% | 75% | Current | Current | 174 | 61 | 31 | 20 | 21
15 | 2.8 | Improved | Current | None | Current | Current | 207 | 91 | 37 | 4 | 4
15 | 2.8 | Improved | Current | 75% | Current | Current | 174 | 56 | 31 | 20 | 21
15 | 2.8 | Improved | 25% | None | Current | Current | 205 | 94 | 37 | 5 | 5
15 | 2.8 | Improved | 25% | 75% | Current | Current | 172 | 59 | 30 | 21 | 22
15 | 4 | Current | Current | None | Current | Current | 202 | 85 | 36 | 7 | 7
15 | 4 | Current | Current | 75% | Current | Current | 168 | 50 | 30 | 22 | 24
15 | 4 | Current | 25% | None | Current | Current | 199 | 88 | 36 | 8 | 8
15 | 4 | Current | 25% | 75% | Current | Current | 166 | 52 | 29 | 23 | 24
15 | 4 | Improved | Current | None | Current | Current | 200 | 83 | 36 | 8 | 8
15 | 4 | Improved | Current | 75% | Current | Current | 166 | 48 | 29 | 23 | 25
15 | 4 | Improved | 25% | None | Current | Current | 197 | 86 | 35 | 9 | 9
15 | 4 | Improved | 25% | 75% | Current | Current | 164 | 50 | 29 | 24 | 25
15 | 5.5 | Current | Current | None | Current | Current | 198 | 81 | 35 | 8 | 9
15 | 5.5 | Current | Current | 75% | Current | Current | 164 | 46 | 29 | 24 | 26
15 | 5.5 | Current | 25% | None | Current | Current | 195 | 84 | 35 | 10 | 10
15 | 5.5 | Current | 25% | 75% | Current | Current | 162 | 48 | 29 | 25 | 26
15 | 5.5 | Improved | Current | None | Current | Current | 196 | 80 | 35 | 9 | 10
15 | 5.5 | Improved | Current | 75% | Current | Current | 162 | 44 | 29 | 25 | 27
15 | 5.5 | Improved | 25% | None | Current | Current | 194 | 82 | 35 | 10 | 11
15 | 5.5 | Improved | 25% | 75% | Current | Current | 160 | 46 | 28 | 26 | 27
5 | 2.8 | Current | Current | None | Improved | Current | 188 | 87 | 34 | 13 | 13
5 | 2.8 | Current | Current | 75% | Improved | Current | 159 | 55 | 28 | 26 | 27
5 | 2.8 | Current | 25% | None | Improved | Current | 186 | 90 | 34 | 14 | 14
5 | 2.8 | Current | 25% | 75% | Improved | Current | 157 | 58 | 28 | 27 | 28
5 | 2.8 | Improved | Current | None | Improved | Current | 187 | 85 | 33 | 14 | 14
5 | 2.8 | Improved | Current | 75% | Improved | Current | 157 | 53 | 28 | 27 | 28
5 | 2.8 | Improved | 25% | None | Improved | Current | 184 | 88 | 33 | 15 | 15
5 | 2.8 | Improved | 25% | 75% | Improved | Current | 155 | 56 | 28 | 28 | 29
5 | 4 | Current | Current | None | Improved | Current | 181 | 79 | 32 | 16 | 17
5 | 4 | Current | Current | 75% | Improved | Current | 151 | 47 | 27 | 30 | 31
5 | 4 | Current | 25% | None | Improved | Current | 179 | 82 | 32 | 17 | 17
5 | 4 | Current | 25% | 75% | Improved | Current | 149 | 50 | 26 | 31 | 32
5 | 4 | Improved | Current | None | Improved | Current | 179 | 77 | 32 | 17 | 17
5 | 4 | Improved | Current | 75% | Improved | Current | 150 | 45 | 26 | 31 | 32
5 | 4 | Improved | 25% | None | Improved | Current | 177 | 80 | 32 | 18 | 18
5 | 4 | Improved | 25% | 75% | Improved | Current | 147 | 48 | 26 | 32 | 33
5 | 5.5 | Current | Current | None | Improved | Current | 177 | 75 | 32 | 18 | 18
5 | 5.5 | Current | Current | 75% | Improved | Current | 148 | 43 | 26 | 32 | 33
5 | 5.5 | Current | 25% | None | Improved | Current | 175 | 77 | 31 | 19 | 19
5 | 5.5 | Current | 25% | 75% | Improved | Current | 145 | 46 | 26 | 33 | 34
5 | 5.5 | Improved | Current | None | Improved | Current | 176 | 73 | 31 | 19 | 19
5 | 5.5 | Improved | Current | 75% | Improved | Current | 146 | 41 | 26 | 33 | 34
5 | 5.5 | Improved | 25% | None | Improved | Current | 173 | 75 | 31 | 20 | 20
5 | 5.5 | Improved | 25% | 75% | Improved | Current | 143 | 43 | 25 | 34 | 35
10 | 2.8 | Current | Current | None | Improved | Current | 183 | 81 | 33 | 15 | 15
10 | 2.8 | Current | Current | 75% | Improved | Current | 154 | 49 | 27 | 29 | 30
10 | 2.8 | Current | 25% | None | Improved | Current | 181 | 84 | 32 | 16 | 16
10 | 2.8 | Current | 25% | 75% | Improved | Current | 152 | 52 | 27 | 30 | 31
10 | 2.8 | Improved | Current | None | Improved | Current | 181 | 79 | 32 | 16 | 16
10 | 2.8 | Improved | Current | 75% | Improved | Current | 152 | 47 | 27 | 30 | 31
10 | 2.8 | Improved | 25% | None | Improved | Current | 179 | 82 | 32 | 17 | 17
10 | 2.8 | Improved | 25% | 75% | Improved | Current | 150 | 50 | 26 | 31 | 32
10 | 4 | Current | Current | None | Improved | Current | 176 | 73 | 31 | 19 | 19
10 | 4 | Current | Current | 75% | Improved | Current | 146 | 41 | 26 | 32 | 34
10 | 4 | Current | 25% | None | Improved | Current | 173 | 76 | 31 | 20 | 20
10 | 4 | Current | 25% | 75% | Improved | Current | 144 | 44 | 25 | 33 | 35
10 | 4 | Improved | Current | None | Improved | Current | 174 | 71 | 31 | 19 | 20
10 | 4 | Improved | Current | 75% | Improved | Current | 144 | 39 | 25 | 33 | 35
10 | 4 | Improved | 25% | None | Improved | Current | 171 | 74 | 31 | 21 | 21
10 | 4 | Improved | 25% | 75% | Improved | Current | 142 | 42 | 25 | 34 | 36
10 | 5.5 | Current | Current | None | Improved | Current | 172 | 69 | 31 | 20 | 21
10 | 5.5 | Current | Current | 75% | Improved | Current | 142 | 37 | 25 | 34 | 36
10 | 5.5 | Current | 25% | None | Improved | Current | 170 | 72 | 30 | 21 | 22
10 | 5.5 | Current | 25% | 75% | Improved | Current | 140 | 40 | 25 | 35 | 37
10 | 5.5 | Improved | Current | None | Improved | Current | 170 | 67 | 30 | 21 | 22
10 | 5.5 | Improved | Current | 75% | Improved | Current | 140 | 35 | 25 | 35 | 37
10 | 5.5 | Improved | 25% | None | Improved | Current | 168 | 70 | 30 | 22 | 23
10 | 5.5 | Improved | 25% | 75% | Improved | Current | 138 | 38 | 24 | 36 | 38
15 | 2.8 | Current | Current | None | Improved | Current | 181 | 79 | 32 | 16 | 16
15 | 2.8 | Current | Current | 75% | Improved | Current | 152 | 47 | 27 | 30 | 31
15 | 2.8 | Current | 25% | None | Improved | Current | 179 | 82 | 32 | 17 | 17
15 | 2.8 | Current | 25% | 75% | Improved | Current | 150 | 50 | 27 | 31 | 32
15 | 2.8 | Improved | Current | None | Improved | Current | 179 | 77 | 32 | 17 | 17
15 | 2.8 | Improved | Current | 75% | Improved | Current | 150 | 45 | 26 | 31 | 32
15 | 2.8 | Improved | 25% | None | Improved | Current | 177 | 80 | 32 | 18 | 18
15 | 2.8 | Improved | 25% | 75% | Improved | Current | 148 | 48 | 26 | 32 | 33
15 | 4 | Current | Current | None | Improved | Current | 174 | 71 | 31 | 19 | 20
15 | 4 | Current | Current | 75% | Improved | Current | 144 | 39 | 25 | 33 | 35
15 | 4 | Current | 25% | None | Improved | Current | 171 | 74 | 31 | 21 | 21
15 | 4 | Current | 25% | 75% | Improved | Current | 142 | 42 | 25 | 34 | 36
15 | 4 | Improved | Current | None | Improved | Current | 172 | 69 | 31 | 20 | 21
15 | 4 | Improved | Current | 75% | Improved | Current | 142 | 37 | 25 | 34 | 36
15 | 4 | Improved | 25% | None | Improved | Current | 170 | 72 | 30 | 21 | 22
15 | 4 | Improved | 25% | 75% | Improved | Current | 140 | 40 | 25 | 35 | 37
15 | 5.5 | Current | Current | None | Improved | Current | 170 | 67 | 30 | 21 | 22
15 | 5.5 | Current | Current | 75% | Improved | Current | 140 | 36 | 25 | 35 | 37
15 | 5.5 | Current | 25% | None | Improved | Current | 168 | 70 | 30 | 22 | 23
15 | 5.5 | Current | 25% | 75% | Improved | Current | 138 | 38 | 24 | 36 | 38
15 | 5.5 | Improved | Current | None | Improved | Current | 168 | 66 | 30 | 22 | 23
15 | 5.5 | Improved | Current | 75% | Improved | Current | 138 | 34 | 24 | 36 | 38
15 | 5.5 | Improved | 25% | None | Improved | Current | 166 | 68 | 30 | 23 | 24
15 | 5.5 | Improved | 25% | 75% | Improved | Current | 136 | 36 | 24 | 37 | 39
5 | 2.8 | Current | Current | None | Improved | ASHP | 150 | 85 | 26 | 31 | 33
5 | 2.8 | Current | Current | 75% | Improved | ASHP | 136 | 55 | 24 | 37 | 39
5 | 2.8 | Current | 25% | None | Improved | ASHP | 146 | 87 | 25 | 32 | 35
5 | 2.8 | Current | 25% | 75% | Improved | ASHP | 133 | 58 | 23 | 39 | 41
5 | 2.8 | Improved | Current | None | Improved | ASHP | 149 | 83 | 26 | 31 | 34
5 | 2.8 | Improved | Current | 75% | Improved | ASHP | 135 | 53 | 23 | 37 | 40
5 | 2.8 | Improved | 25% | None | Improved | ASHP | 145 | 86 | 25 | 33 | 35
5 | 2.8 | Improved | 25% | 75% | Improved | ASHP | 132 | 56 | 23 | 39 | 41
5 | 4 | Current | Current | None | Improved | ASHP | 146 | 78 | 25 | 32 | 35
5 | 4 | Current | Current | 75% | Improved | ASHP | 132 | 47 | 23 | 39 | 41
5 | 4 | Current | 25% | None | Improved | ASHP | 143 | 80 | 25 | 34 | 36
5 | 4 | Current | 25% | 75% | Improved | ASHP | 129 | 50 | 22 | 40 | 43
5 | 4 | Improved | Current | None | Improved | ASHP | 145 | 76 | 25 | 33 | 35
5 | 4 | Improved | Current | 75% | Improved | ASHP | 131 | 45 | 23 | 39 | 42
5 | 4 | Improved | 25% | None | Improved | ASHP | 142 | 78 | 25 | 34 | 37
5 | 4 | Improved | 25% | 75% | Improved | ASHP | 128 | 48 | 22 | 41 | 43
5 | 5.5 | Current | Current | None | Improved | ASHP | 145 | 74 | 25 | 33 | 36
5 | 5.5 | Current | Current | 75% | Improved | ASHP | 131 | 43 | 23 | 40 | 42
5 | 5.5 | Current | 25% | None | Improved | ASHP | 141 | 76 | 24 | 35 | 37
5 | 5.5 | Current | 25% | 75% | Improved | ASHP | 127 | 46 | 22 | 41 | 44
5 | 5.5 | Improved | Current | None | Improved | ASHP | 144 | 72 | 25 | 33 | 36
5 | 5.5 | Improved | Current | 75% | Improved | ASHP | 130 | 41 | 22 | 40 | 42
5 | 5.5 | Improved | 25% | None | Improved | ASHP | 140 | 75 | 24 | 35 | 38
5 | 5.5 | Improved | 25% | 75% | Improved | ASHP | 126 | 44 | 22 | 42 | 44
10 | 2.8 | Current | Current | None | Improved | ASHP | 147 | 80 | 26 | 32 | 34
10 | 2.8 | Current | Current | 75% | Improved | ASHP | 134 | 49 | 23 | 38 | 41
10 | 2.8 | Current | 25% | None | Improved | ASHP | 144 | 82 | 25 | 33 | 36
10 | 2.8 | Current | 25% | 75% | Improved | ASHP | 130 | 52 | 22 | 40 | 42
10 | 2.8 | Improved | Current | None | Improved | ASHP | 146 | 78 | 25 | 32 | 35
10 | 2.8 | Improved | Current | 75% | Improved | ASHP | 133 | 47 | 23 | 39 | 41
10 | 2.8 | Improved | 25% | None | Improved | ASHP | 143 | 81 | 25 | 34 | 36
10 | 2.8 | Improved | 25% | 75% | Improved | ASHP | 129 | 50 | 22 | 40 | 43
10 | 4 | Current | Current | None | Improved | ASHP | 144 | 73 | 25 | 33 | 36
10 | 4 | Current | Current | 75% | Improved | ASHP | 130 | 41 | 22 | 40 | 42
10 | 4 | Current | 25% | None | Improved | ASHP | 140 | 75 | 24 | 35 | 38
10 | 4 | Current | 25% | 75% | Improved | ASHP | 126 | 44 | 22 | 42 | 44
10 | 4 | Improved | Current | None | Improved | ASHP | 143 | 71 | 25 | 34 | 36
10 | 4 | Improved | Current | 75% | Improved | ASHP | 129 | 39 | 22 | 40 | 43
10 | 4 | Improved | 25% | None | Improved | ASHP | 139 | 73 | 24 | 36 | 38
10 | 4 | Improved | 25% | 75% | Improved | ASHP | 125 | 42 | 22 | 42 | 45
10 | 5.5 | Current | Current | None | Improved | ASHP | 142 | 69 | 25 | 34 | 37
10 | 5.5 | Current | Current | 75% | Improved | ASHP | 128 | 37 | 22 | 41 | 43
10 | 5.5 | Current | 25% | None | Improved | ASHP | 138 | 71 | 24 | 36 | 38
10 | 5.5 | Current | 25% | 75% | Improved | ASHP | 124 | 40 | 21 | 43 | 45
10 | 5.5 | Improved | Current | None | Improved | ASHP | 141 | 67 | 24 | 35 | 37
10 | 5.5 | Improved | Current | 75% | Improved | ASHP | 127 | 36 | 22 | 41 | 44
10 | 5.5 | Improved | 25% | None | Improved | ASHP | 137 | 69 | 24 | 36 | 39
10 | 5.5 | Improved | 25% | 75% | Improved | ASHP | 123 | 38 | 21 | 43 | 45
15 | 2.8 | Current | Current | None | Improved | ASHP | 147 | 78 | 25 | 32 | 35
15 | 2.8 | Current | Current | 75% | Improved | ASHP | 133 | 47 | 23 | 39 | 41
15 | 2.8 | Current | 25% | None | Improved | ASHP | 143 | 81 | 25 | 34 | 36
15 | 2.8 | Current | 25% | 75% | Improved | ASHP | 129 | 50 | 22 | 40 | 43
15 | 2.8 | Improved | Current | None | Improved | ASHP | 146 | 76 | 25 | 33 | 35
15 | 2.8 | Improved | Current | 75% | Improved | ASHP | 132 | 45 | 23 | 39 | 42
15 | 2.8 | Improved | 25% | None | Improved | ASHP | 142 | 79 | 25 | 34 | 37
15 | 2.8 | Improved | 25% | 75% | Improved | ASHP | 128 | 48 | 22 | 41 | 43
15 | 4 | Current | Current | None | Improved | ASHP | 143 | 71 | 25 | 34 | 36
15 | 4 | Current | Current | 75% | Improved | ASHP | 129 | 39 | 22 | 40 | 43
15 | 4 | Current | 25% | None | Improved | ASHP | 139 | 73 | 24 | 36 | 38
15 | 4 | Current | 25% | 75% | Improved | ASHP | 125 | 42 | 22 | 42 | 45
15 | 4 | Improved | Current | None | Improved | ASHP | 142 | 69 | 25 | 34 | 37
15 | 4 | Improved | Current | 75% | Improved | ASHP | 128 | 38 | 22 | 41 | 43
15 | 4 | Improved | 25% | None | Improved | ASHP | 138 | 71 | 24 | 36 | 38
15 | 4 | Improved | 25% | 75% | Improved | ASHP | 124 | 40 | 21 | 43 | 45
15 | 5.5 | Current | Current | None | Improved | ASHP | 141 | 67 | 24 | 35 | 37
15 | 5.5 | Current | Current | 75% | Improved | ASHP | 127 | 36 | 22 | 41 | 44
15 | 5.5 | Current | 25% | None | Improved | ASHP | 137 | 69 | 24 | 36 | 39
15 | 5.5 | Current | 25% | 75% | Improved | ASHP | 123 | 38 | 21 | 43 | 45
15 | 5.5 | Improved | Current | None | Improved | ASHP | 140 | 65 | 24 | 35 | 38
15 | 5.5 | Improved | Current | 75% | Improved | ASHP | 126 | 34 | 22 | 42 | 44
15 | 5.5 | Improved | 25% | None | Improved | ASHP | 136 | 67 | 24 | 37 | 39
15 | 5.5 | Improved | 25% | 75% | Improved | ASHP | 122 | 36 | 21 | 43 | 46