## Final
Spandrels R(ft2·°F·h/BTU) | Glass R(ft2·°F·h/BTU) | Air Leakage | LPD | ERV | Controls | HVAC System | Solar PV | Electricity kWh | Natural Gas kWh | Total Energy kWh | TEUI kWh/m² | TEDI kWh/m² | GHGI kgCO2/m² | En Saving % | GHG Saving%
5 | 2.8 | Current | Current | None | Current | Current | No | 11827263.0183 | 11604177.1 | 23431440.1183 | 215.9384 | 100.9439 | 38.8484 | 0% | 0%
5 | 2.8 | Current | Current | 75% | Current | Current | No | 12188437.9884 | 7677596.2 | 19866034.1884 | 183.0805 | 65.5869 | 32.5388 | 15.22% | 16.24%
5 | 2.8 | Current | 25% | None | Current | Current | No | 11303698.0618 | 11891141.3 | 23194839.3618 | 213.758 | 103.6877 | 38.5306 | 1.01% | 0.818%
5 | 2.8 | Current | 25% | 75% | Current | Current | No | 11666316.0317 | 7972383.5 | 19638699.5317 | 180.9855 | 68.3266 | 32.237 | 16.19% | 17.02%
5 | 2.8 | Improved | Current | None | Current | Current | No | 11828447.0182 | 11403970.2 | 23232417.2182 | 214.1043 | 98.9763 | 38.4997 | 0.8494% | 0.8976%
5 | 2.8 | Improved | Current | 75% | Current | Current | No | 12189692.9883 | 7470796.8 | 19660489.7883 | 181.1863 | 63.6202 | 32.1786 | 16.09% | 17.17%
5 | 2.8 | Improved | 25% | None | Current | Current | No | 11303910.0618 | 11684224.7 | 22988134.7618 | 211.853 | 101.693 | 38.1686 | 1.892% | 1.75%
5 | 2.8 | Improved | 25% | 75% | Current | Current | No | 11666718.0317 | 7766375.2 | 19433093.2317 | 179.0906 | 66.3327 | 31.8769 | 17.06% | 17.95%
5 | 4 | Current | Current | None | Current | Current | No | 11840697.0172 | 10787908.4 | 22628605.4172 | 208.5397 | 92.9113 | 37.4401 | 3.426% | 3.625%
5 | 4 | Current | Current | 75% | Current | Current | No | 12201176.9873 | 6831881 | 19033057.9873 | 175.404 | 57.5606 | 31.0779 | 18.77% | 20%
5 | 4 | Current | 25% | None | Current | Current | No | 11313475.061 | 11053923.1 | 22367398.161 | 206.1325 | 95.5177 | 37.0799 | 4.541% | 4.552%
5 | 4 | Current | 25% | 75% | Current | Current | No | 11676213.0309 | 7115885.9 | 18792098.9309 | 173.1834 | 60.1614 | 30.7527 | 19.8% | 20.84%
5 | 4 | Improved | Current | None | Current | Current | No | 11843899.017 | 10587906.6 | 22431805.617 | 206.726 | 90.9407 | 37.0949 | 4.266% | 4.513%
5 | 4 | Improved | Current | 75% | Current | Current | No | 12204442.987 | 6622093 | 18826535.987 | 173.5008 | 55.5928 | 30.7157 | 19.65% | 20.93%
5 | 4 | Improved | 25% | None | Current | Current | No | 11315829.0608 | 10850551.8 | 22166380.8608 | 204.2799 | 93.5131 | 36.7275 | 5.399% | 5.459%
5 | 4 | Improved | 25% | 75% | Current | Current | No | 11678725.0307 | 6907445.7 | 18586170.7307 | 171.2856 | 58.1587 | 30.3917 | 20.68% | 21.77%
5 | 5.5 | Current | Current | None | Current | Current | No | 11850580.0164 | 10383832.1 | 22234412.1164 | 204.9069 | 88.9258 | 36.7481 | 5.109% | 5.406%
5 | 5.5 | Current | Current | 75% | Current | Current | No | 12210641.9865 | 6406679.4 | 18617321.3865 | 171.5727 | 53.5802 | 30.3482 | 20.55% | 21.88%
5 | 5.5 | Current | 25% | None | Current | Current | No | 11321347.0603 | 10642932 | 21964279.0603 | 202.4174 | 91.4476 | 36.3726 | 6.262% | 6.373%
5 | 5.5 | Current | 25% | 75% | Current | Current | No | 11683878.0302 | 6689688.1 | 18373566.1302 | 169.3263 | 56.0956 | 30.0185 | 21.59% | 22.73%
5 | 5.5 | Improved | Current | None | Current | Current | No | 11855250.016 | 10181164 | 22036414.016 | 203.0822 | 86.9612 | 36.4005 | 5.954% | 6.301%
5 | 5.5 | Improved | Current | 75% | Current | Current | No | 12215403.9861 | 6196276.1 | 18411680.0861 | 169.6775 | 51.6187 | 29.9872 | 21.42% | 22.81%
5 | 5.5 | Improved | 25% | None | Current | Current | No | 11324809.06 | 10440293.2 | 21765102.26 | 200.5819 | 89.444 | 36.0232 | 7.112% | 7.272%
5 | 5.5 | Improved | 25% | 75% | Current | Current | No | 11687454.0299 | 6475446.5 | 18162900.5299 | 167.3849 | 54.0943 | 29.6489 | 22.48% | 23.68%
10 | 2.8 | Current | Current | None | Current | Current | No | 11827896.0183 | 11032446.2 | 22860342.2183 | 210.6753 | 95.3042 | 37.8483 | 2.437% | 2.574%
10 | 2.8 | Current | Current | 75% | Current | Current | No | 12188284.9884 | 7085120.9 | 19273405.8884 | 177.619 | 59.9494 | 31.5011 | 17.75% | 18.91%
10 | 2.8 | Current | 25% | None | Current | Current | No | 11302694.0619 | 11305375.7 | 22608069.7619 | 208.3504 | 97.9846 | 37.5033 | 3.514% | 3.462%
10 | 2.8 | Current | 25% | 75% | Current | Current | No | 11665153.0318 | 7377417.7 | 19042570.7318 | 175.4917 | 62.6255 | 31.1934 | 18.73% | 19.7%
10 | 2.8 | Improved | Current | None | Current | Current | No | 11829221.0182 | 10831125.9 | 22660346.9182 | 208.8322 | 93.3227 | 37.4978 | 3.291% | 3.476%
10 | 2.8 | Improved | Current | 75% | Current | Current | No | 12189950.9882 | 6877618.3 | 19067569.2882 | 175.7221 | 57.9699 | 31.1404 | 18.62% | 19.84%
10 | 2.8 | Improved | 25% | None | Current | Current | No | 11303518.0618 | 11102033.7 | 22405551.7618 | 206.4841 | 95.972 | 37.1486 | 4.378% | 4.375%
10 | 2.8 | Improved | 25% | 75% | Current | Current | No | 11666149.0317 | 7165871.7 | 18832020.7317 | 173.5513 | 60.6139 | 30.8245 | 19.63% | 20.65%
10 | 4 | Current | Current | None | Current | Current | No | 11843882.017 | 10219195.4 | 22063077.417 | 203.3279 | 87.2954 | 36.4493 | 5.84% | 6.175%
10 | 4 | Current | Current | 75% | Current | Current | No | 12203733.9871 | 6233692.2 | 18437426.1871 | 169.9148 | 51.9506 | 30.0345 | 21.31% | 22.69%
10 | 4 | Current | 25% | None | Current | Current | No | 11315082.0608 | 10480434.2 | 21795516.2608 | 200.8622 | 89.8088 | 36.0783 | 6.982% | 7.131%
10 | 4 | Current | 25% | 75% | Current | Current | No | 11677331.0308 | 6514386.2 | 18191717.2308 | 167.6504 | 54.4565 | 29.7013 | 22.36% | 23.55%
10 | 4 | Improved | Current | None | Current | Current | No | 11847414.0167 | 10014945.1 | 21862359.1167 | 201.4782 | 85.3234 | 36.0972 | 6.696% | 7.082%
10 | 4 | Improved | Current | 75% | Current | Current | No | 12207715.9868 | 6019479.9 | 18227195.8868 | 167.9774 | 49.9821 | 29.6656 | 22.21% | 23.64%
10 | 4 | Improved | 25% | None | Current | Current | No | 11318717.0605 | 10273957.1 | 21592674.1605 | 198.9928 | 87.7911 | 35.7224 | 7.847% | 8.047%
10 | 4 | Improved | 25% | 75% | Current | Current | No | 11680923.0305 | 6299207 | 17980130.0305 | 165.7005 | 52.4417 | 29.3301 | 23.26% | 24.5%
10 | 5.5 | Current | Current | None | Current | Current | No | 11854763.0161 | 9816437.6 | 21671200.6161 | 199.7165 | 83.3502 | 35.7611 | 7.512% | 7.947%
10 | 5.5 | Current | Current | 75% | Current | Current | No | 12214169.9862 | 5805121.1 | 18019291.0862 | 166.0614 | 48.0133 | 29.3004 | 23.1% | 24.58%
10 | 5.5 | Current | 25% | None | Current | Current | No | 11325075.06 | 10065604.8 | 21390679.86 | 197.1313 | 85.7532 | 35.3676 | 8.709% | 8.96%
10 | 5.5 | Current | 25% | 75% | Current | Current | No | 11686581.03 | 6076292.6 | 17762873.63 | 163.6983 | 50.4073 | 28.9487 | 24.19% | 25.48%
10 | 5.5 | Improved | Current | None | Current | Current | No | 11859379.0157 | 9619951.8 | 21479330.8157 | 197.9483 | 81.4002 | 35.4243 | 8.331% | 8.814%
10 | 5.5 | Improved | Current | 75% | Current | Current | No | 12218871.9858 | 5593868.1 | 17812740.0858 | 164.1579 | 46.0679 | 28.9379 | 23.98% | 25.51%
10 | 5.5 | Improved | 25% | None | Current | Current | No | 11329175.0597 | 9861032.2 | 21190207.2597 | 195.2838 | 83.7435 | 35.0158 | 9.565% | 9.865%
10 | 5.5 | Improved | 25% | 75% | Current | Current | No | 11690789.0297 | 5857275.1 | 17548064.1297 | 161.7187 | 48.4007 | 28.5718 | 25.11% | 26.45%
15 | 2.8 | Current | Current | None | Current | Current | No | 11827622.0183 | 10836487.8 | 22664109.8183 | 208.8669 | 93.3625 | 37.5047 | 3.275% | 3.459%
15 | 2.8 | Current | Current | 75% | Current | Current | No | 12187754.9884 | 6880929.2 | 19068684.1884 | 175.7323 | 58.0092 | 31.1428 | 18.62% | 19.84%
15 | 2.8 | Current | 25% | None | Current | Current | No | 11302525.0619 | 11108567.6 | 22411092.6619 | 206.5352 | 96.0175 | 37.1585 | 4.355% | 4.35%
15 | 2.8 | Current | 25% | 75% | Current | Current | No | 11664716.0318 | 7172317.7 | 18837033.7318 | 173.5975 | 60.6592 | 30.8335 | 19.61% | 20.63%
15 | 2.8 | Improved | Current | None | Current | Current | No | 11829752.0181 | 10637130.6 | 22466882.6181 | 207.0493 | 91.3767 | 37.159 | 4.117% | 4.349%
15 | 2.8 | Improved | Current | 75% | Current | Current | No | 12190153.9882 | 6669266 | 18859419.9882 | 173.8038 | 56.0256 | 30.7759 | 19.51% | 20.78%
15 | 2.8 | Improved | 25% | None | Current | Current | No | 11303836.0618 | 10905723.7 | 22209559.7618 | 204.6779 | 93.9973 | 36.8053 | 5.215% | 5.259%
15 | 2.8 | Improved | 25% | 75% | Current | Current | No | 11666154.0317 | 6960068.5 | 18626222.5317 | 171.6547 | 58.6404 | 30.4641 | 20.51% | 21.58%
15 | 4 | Current | Current | None | Current | Current | No | 11844499.0169 | 10020453.5 | 21864952.5169 | 201.5021 | 85.3711 | 36.1023 | 6.685% | 7.069%
15 | 4 | Current | Current | 75% | Current | Current | No | 12204400.987 | 6024285.1 | 18228686.087 | 167.9911 | 50.0292 | 29.6689 | 22.2% | 23.63%
15 | 4 | Current | 25% | None | Current | Current | No | 11316126.0608 | 10280608.2 | 21596734.2608 | 199.0302 | 87.8434 | 35.73 | 7.83% | 8.027%
15 | 4 | Current | 25% | 75% | Current | Current | No | 11677995.0307 | 6304100.1 | 17982095.1307 | 165.7186 | 52.4929 | 29.3341 | 23.26% | 24.49%
15 | 4 | Improved | Current | None | Current | Current | No | 11848761.0166 | 9821067 | 21669828.0166 | 199.7038 | 83.4013 | 35.7598 | 7.518% | 7.95%
15 | 4 | Improved | Current | 75% | Current | Current | No | 12208485.9867 | 5810893.2 | 18019379.1867 | 166.0622 | 48.0634 | 29.3016 | 23.1% | 24.57%
15 | 4 | Improved | 25% | None | Current | Current | No | 11319665.0605 | 10072812.6 | 21392477.6605 | 197.1478 | 85.8236 | 35.3717 | 8.702% | 8.949%
15 | 4 | Improved | 25% | 75% | Current | Current | No | 11681627.0304 | 6084438 | 17766065.0304 | 163.7277 | 50.4765 | 28.9552 | 24.18% | 25.47%
15 | 5.5 | Current | Current | None | Current | Current | No | 11855584.016 | 9625284.4 | 21480868.416 | 197.9624 | 81.4506 | 35.4277 | 8.325% | 8.805%
15 | 5.5 | Current | Current | 75% | Current | Current | No | 12214936.9862 | 5598087.3 | 17813024.2862 | 164.1605 | 46.1171 | 28.9391 | 23.98% | 25.51%
15 | 5.5 | Current | 25% | None | Current | Current | No | 11326194.0599 | 9867361 | 21193555.0599 | 195.3146 | 83.7981 | 35.0222 | 9.551% | 9.849%
15 | 5.5 | Current | 25% | 75% | Current | Current | No | 11687454.0299 | 5863047.2 | 17550501.2299 | 161.7411 | 48.4542 | 28.5766 | 25.1% | 26.44%
15 | 5.5 | Improved | Current | None | Current | Current | No | 11856234.0159 | 9400524.1 | 21256758.1159 | 195.8971 | 79.5074 | 35.0352 | 9.281% | 9.816%
15 | 5.5 | Improved | Current | 75% | Current | Current | No | 12215402.9861 | 5359995.5 | 17575398.4861 | 161.9706 | 44.1801 | 28.5229 | 24.99% | 26.58%
15 | 5.5 | Improved | 25% | None | Current | Current | No | 11330349.0596 | 9667447.1 | 20997796.1596 | 193.5106 | 81.7918 | 34.6787 | 10.39% | 10.73%
15 | 5.5 | Improved | 25% | 75% | Current | Current | No | 11691584.0296 | 5645582.6 | 17337166.6296 | 159.7751 | 46.4526 | 28.2023 | 26.01% | 27.4%
5 | 2.8 | Current | Current | None | Improved | Current | No | 10660237.1152 | 9782303.1 | 20442540.2152 | 188.3935 | 86.9803 | 33.8299 | 12.76% | 12.92%
5 | 2.8 | Current | Current | 75% | Improved | Current | No | 10995001.0874 | 6274360.6 | 17269361.6874 | 159.1502 | 54.992 | 28.212 | 26.3% | 27.38%
5 | 2.8 | Current | 25% | None | Improved | Current | No | 10134728.1588 | 10069355.2 | 20204083.3588 | 186.1959 | 89.724 | 33.5092 | 13.77% | 13.74%
5 | 2.8 | Current | 25% | 75% | Improved | Current | No | 10469821.131 | 6568122.4 | 17037943.531 | 157.0175 | 57.7317 | 27.9036 | 27.29% | 28.17%
5 | 2.8 | Improved | Current | None | Improved | Current | No | 10660853.1151 | 9582096.2 | 20242949.3151 | 186.5541 | 85.0128 | 33.4803 | 13.61% | 13.82%
5 | 2.8 | Improved | Current | 75% | Improved | Current | No | 10996120.0873 | 6066887.3 | 17063007.3873 | 157.2485 | 53.0252 | 27.8505 | 27.18% | 28.31%
5 | 2.8 | Improved | 25% | None | Improved | Current | No | 10134184.1589 | 9862907.4 | 19997091.5589 | 184.2883 | 87.7294 | 33.1469 | 14.66% | 14.68%
5 | 2.8 | Improved | 25% | 75% | Improved | Current | No | 10470035.131 | 6362641.5 | 16832676.631 | 155.1258 | 55.7377 | 27.5441 | 28.16% | 29.1%
5 | 4 | Current | Current | None | Improved | Current | No | 10672324.1142 | 8965096.8 | 19637420.9142 | 180.9737 | 78.9477 | 32.4179 | 16.19% | 16.55%
5 | 4 | Current | Current | 75% | Improved | Current | No | 11008202.0863 | 5428059.4 | 16436261.4863 | 151.4726 | 46.9655 | 26.7508 | 29.85% | 31.14%
5 | 4 | Current | 25% | None | Improved | Current | No | 10143109.1581 | 9231375.2 | 19374484.3581 | 178.5505 | 81.5542 | 32.0551 | 17.31% | 17.49%
5 | 4 | Current | 25% | 75% | Improved | Current | No | 10479977.1302 | 5712591.7 | 16192568.8302 | 149.2268 | 49.5665 | 26.4215 | 30.89% | 31.99%
5 | 4 | Improved | Current | None | Improved | Current | No | 10675007.114 | 8765475.9 | 19440483.014 | 179.1587 | 76.9771 | 32.0726 | 17.03% | 17.44%
5 | 4 | Improved | Current | 75% | Improved | Current | No | 11010967.0861 | 5218154.2 | 16229121.2861 | 149.5636 | 44.9978 | 26.3876 | 30.74% | 32.08%
5 | 4 | Improved | 25% | None | Improved | Current | No | 10144736.158 | 9027652.3 | 19172388.458 | 176.688 | 79.5496 | 31.7009 | 18.18% | 18.4%
5 | 4 | Improved | 25% | 75% | Improved | Current | No | 10482204.13 | 5504122.2 | 15986326.33 | 147.3261 | 47.5637 | 26.0599 | 31.77% | 32.92%
5 | 5.5 | Current | Current | None | Improved | Current | No | 10681454.1134 | 8560581 | 19242035.1134 | 177.3299 | 74.9621 | 31.7239 | 17.88% | 18.34%
5 | 5.5 | Current | Current | 75% | Improved | Current | No | 11017349.0856 | 5002389 | 16019738.0856 | 147.634 | 42.9852 | 26.0198 | 31.63% | 33.02%
5 | 5.5 | Current | 25% | None | Improved | Current | No | 10149898.1576 | 8819768.8 | 18969666.9576 | 174.8198 | 77.4841 | 31.345 | 19.04% | 19.31%
5 | 5.5 | Current | 25% | 75% | Improved | Current | No | 10487556.1295 | 5285339.1 | 15772895.2295 | 145.3591 | 45.5006 | 25.6852 | 32.68% | 33.88%
5 | 5.5 | Improved | Current | None | Improved | Current | No | 10685484.1131 | 8358498.9 | 19043983.0131 | 175.5047 | 72.9975 | 31.3764 | 18.72% | 19.23%
5 | 5.5 | Improved | Current | 75% | Improved | Current | No | 11021634.0852 | 4791839.2 | 15813473.2852 | 145.7331 | 41.0238 | 25.6578 | 32.51% | 33.95%
5 | 5.5 | Improved | 25% | None | Improved | Current | No | 10152629.1573 | 8617305.8 | 18769934.9573 | 172.9791 | 75.4804 | 30.9948 | 19.89% | 20.22%
5 | 5.5 | Improved | 25% | 75% | Improved | Current | No | 10490660.1293 | 5071390.5 | 15562050.6293 | 143.4161 | 43.4992 | 25.3155 | 33.58% | 34.84%
10 | 2.8 | Current | Current | None | Improved | Current | No | 10660402.1152 | 9210103.4 | 19870505.5152 | 183.1217 | 81.3405 | 32.8283 | 15.2% | 15.5%
10 | 2.8 | Current | Current | 75% | Improved | Current | No | 10995727.0874 | 5681182.1 | 16676909.1874 | 153.6903 | 49.3545 | 27.1745 | 28.83% | 30.05%
10 | 2.8 | Current | 25% | None | Improved | Current | No | 10133436.1589 | 9483238 | 19616674.1589 | 180.7825 | 84.0211 | 32.4809 | 16.28% | 16.39%
10 | 2.8 | Current | 25% | 75% | Improved | Current | No | 10469293.131 | 5974797.4 | 16444090.531 | 151.5447 | 52.0305 | 26.8638 | 29.82% | 30.85%
10 | 2.8 | Improved | Current | None | Improved | Current | No | 10660985.1151 | 9008871 | 19669856.1151 | 181.2726 | 79.3591 | 32.4768 | 16.05% | 16.4%
10 | 2.8 | Improved | Current | 75% | Improved | Current | No | 10997008.0872 | 5473708.8 | 16470716.8872 | 151.7901 | 47.3749 | 26.8132 | 29.71% | 30.98%
10 | 2.8 | Improved | 25% | None | Improved | Current | No | 10133507.1589 | 9279866.7 | 19413373.8589 | 178.9089 | 82.0082 | 32.1249 | 17.15% | 17.31%
10 | 2.8 | Improved | 25% | 75% | Improved | Current | No | 10470059.131 | 5762548.2 | 16232607.331 | 149.5957 | 50.0189 | 26.4934 | 30.72% | 31.8%
10 | 4 | Current | Current | None | Improved | Current | No | 10675214.114 | 8395651.3 | 19070865.414 | 175.7524 | 73.3319 | 31.4254 | 18.61% | 19.11%
10 | 4 | Current | Current | 75% | Improved | Current | No | 11010966.0861 | 4829636.2 | 15840602.2861 | 145.9831 | 41.3556 | 25.7073 | 32.4% | 33.83%
10 | 4 | Current | 25% | None | Improved | Current | No | 10143797.1581 | 8657974.2 | 18801771.3581 | 173.2725 | 75.8453 | 31.0521 | 19.76% | 20.07%
10 | 4 | Current | 25% | 75% | Improved | Current | No | 10481655.13 | 5111033.4 | 15592688.53 | 143.6984 | 43.8616 | 25.3708 | 33.45% | 34.69%
10 | 4 | Improved | Current | None | Improved | Current | No | 10677974.1137 | 8192045.6 | 18870019.7137 | 173.9015 | 71.3597 | 31.0732 | 19.47% | 20.01%
10 | 4 | Improved | Current | 75% | Improved | Current | No | 11014378.0858 | 4615570.4 | 15629948.4858 | 144.0418 | 39.3871 | 25.3378 | 33.29% | 34.78%
10 | 4 | Improved | 25% | None | Improved | Current | No | 10146765.1578 | 8450764.6 | 18597529.7578 | 171.3903 | 73.8273 | 30.694 | 20.63% | 20.99%
10 | 4 | Improved | 25% | 75% | Improved | Current | No | 10484708.1298 | 4895180.3 | 15379888.4298 | 141.7373 | 41.8467 | 24.9976 | 34.36% | 35.65%
10 | 5.5 | Current | Current | None | Improved | Current | No | 10684864.1132 | 7992981.4 | 18677845.5132 | 172.1305 | 69.3864 | 30.7354 | 20.29% | 20.88%
10 | 5.5 | Current | Current | 75% | Improved | Current | No | 11020808.0853 | 4399570.8 | 15420378.8853 | 142.1104 | 37.4182 | 24.9697 | 34.19% | 35.73%
10 | 5.5 | Current | 25% | None | Improved | Current | No | 10152323.1574 | 8243437.8 | 18395760.9574 | 169.5308 | 71.7897 | 30.3396 | 21.49% | 21.9%
10 | 5.5 | Current | 25% | 75% | Improved | Current | No | 10490420.1293 | 4672441.7 | 15162861.8293 | 139.7372 | 39.8123 | 24.6165 | 35.29% | 36.63%
10 | 5.5 | Improved | Current | None | Improved | Current | No | 10688462.1129 | 7796642.1 | 18485104.2129 | 170.3542 | 67.4362 | 30.3973 | 21.11% | 21.75%
10 | 5.5 | Improved | Current | 75% | Improved | Current | No | 11024682.085 | 4189138.2 | 15213820.285 | 140.2068 | 35.4729 | 24.6073 | 35.07% | 36.66%
10 | 5.5 | Improved | 25% | None | Improved | Current | No | 10155589.1571 | 8037927.6 | 18193516.7571 | 167.667 | 69.7798 | 29.9849 | 22.35% | 22.82%
10 | 5.5 | Improved | 25% | 75% | Improved | Current | No | 10494016.129 | 4453307 | 14947323.129 | 137.7509 | 37.8056 | 24.2385 | 36.21% | 37.61%
15 | 2.8 | Current | Current | None | Improved | Current | No | 10659793.1152 | 9013881.3 | 19673674.4152 | 181.3078 | 79.3989 | 32.4837 | 16.04% | 16.38%
15 | 2.8 | Current | Current | 75% | Improved | Current | No | 10995452.0874 | 5477664.3 | 16473116.3874 | 151.8122 | 47.4141 | 26.8177 | 29.7% | 30.97%
15 | 2.8 | Current | 25% | None | Improved | Current | No | 10132920.159 | 9286224.8 | 19419144.959 | 178.9621 | 82.0538 | 32.1351 | 17.12% | 17.28%
15 | 2.8 | Current | 25% | 75% | Improved | Current | No | 10469094.1311 | 5769170 | 16238264.1311 | 149.6479 | 50.0642 | 26.5035 | 30.7% | 31.78%
15 | 2.8 | Improved | Current | None | Improved | Current | No | 10661362.1151 | 8813586.5 | 19474948.6151 | 179.4764 | 77.4131 | 32.1355 | 16.89% | 17.28%
15 | 2.8 | Improved | Current | 75% | Improved | Current | No | 10997347.0872 | 5265122.1 | 16262469.1872 | 149.8709 | 45.4306 | 26.4485 | 30.6% | 31.92%
15 | 2.8 | Improved | 25% | None | Improved | Current | No | 10133481.1589 | 9082414 | 19215895.1589 | 177.089 | 80.0337 | 31.7792 | 17.99% | 18.2%
15 | 2.8 | Improved | 25% | 75% | Improved | Current | No | 10470291.131 | 5556715.7 | 16027006.831 | 147.701 | 48.0455 | 26.1334 | 31.6% | 32.73%
15 | 4 | Current | Current | None | Improved | Current | No | 10675472.1139 | 8196938.7 | 18872410.8139 | 173.9235 | 71.4076 | 31.0778 | 19.46% | 20%
15 | 4 | Current | Current | 75% | Improved | Current | No | 11011607.086 | 4619467.3 | 15631074.386 | 144.0522 | 39.4342 | 25.3403 | 33.29% | 34.77%
15 | 4 | Current | 25% | None | Improved | Current | No | 10144369.158 | 8457679.4 | 18602048.558 | 171.4319 | 73.8798 | 30.7023 | 20.61% | 20.97%
15 | 4 | Current | 25% | 75% | Improved | Current | No | 10482420.13 | 4900454.3 | 15382874.43 | 141.7648 | 41.898 | 25.0032 | 34.35% | 35.64%
15 | 4 | Improved | Current | None | Improved | Current | No | 10678756.1137 | 7997991.7 | 18676747.8137 | 172.1203 | 69.4375 | 30.7346 | 20.29% | 20.89%
15 | 4 | Improved | Current | 75% | Improved | Current | No | 11015084.0857 | 4406192.6 | 15421276.6857 | 142.1187 | 37.4684 | 24.9723 | 34.19% | 35.72%
15 | 4 | Improved | 25% | None | Improved | Current | No | 10147061.1578 | 8250557.7 | 18397618.8578 | 169.548 | 71.8598 | 30.3439 | 21.48% | 21.89%
15 | 4 | Improved | 25% | 75% | Improved | Current | No | 10485427.1297 | 4680440.6 | 15165867.7297 | 139.7649 | 39.8815 | 24.6227 | 35.28% | 36.62%
15 | 5.5 | Current | Current | None | Improved | Current | No | 10685236.1131 | 7801623.1 | 18486859.2131 | 170.3704 | 67.4867 | 30.4009 | 21.1% | 21.74%
15 | 5.5 | Current | Current | 75% | Improved | Current | No | 11021309.0852 | 4193474.6 | 15214783.6852 | 140.2157 | 35.5221 | 24.6096 | 35.07% | 36.65%
15 | 5.5 | Current | 25% | None | Improved | Current | No | 10153044.1573 | 8044490.8 | 18197534.9573 | 167.704 | 69.8343 | 29.9924 | 22.34% | 22.8%
15 | 5.5 | Current | 25% | 75% | Improved | Current | No | 10491290.1292 | 4459489.3 | 14950779.4292 | 137.7827 | 37.8592 | 24.245 | 36.19% | 37.59%
15 | 5.5 | Improved | Current | None | Improved | Current | No | 10683991.1132 | 7595175.3 | 18279166.4132 | 168.4563 | 65.5459 | 30.0375 | 21.99% | 22.68%
15 | 5.5 | Improved | Current | 75% | Improved | Current | No | 11020493.0853 | 3973197.2 | 14993690.2853 | 138.1782 | 33.5874 | 24.2226 | 36.01% | 37.65%
15 | 5.5 | Improved | 25% | None | Improved | Current | No | 10156071.157 | 7843932.3 | 18000003.457 | 165.8836 | 67.828 | 29.646 | 23.18% | 23.69%
15 | 5.5 | Improved | 25% | 75% | Improved | Current | No | 10494565.129 | 4241995.4 | 14736560.529 | 135.8085 | 35.8576 | 23.8693 | 37.11% | 38.56%
5 | 2.8 | Current | Current | None | Improved | ASHP | No | 13744396.8592 | 2526392.5 | 16270789.3592 | 149.9476 | 84.825 | 25.9567 | 30.56% | 33.18%
5 | 2.8 | Current | Current | 75% | Improved | ASHP | No | 12909240.9285 | 1888326.4 | 14797567.3285 | 136.3708 | 55.0185 | 23.5311 | 36.85% | 39.43%
5 | 2.8 | Current | 25% | None | Improved | ASHP | No | 13318036.8946 | 2560790.7 | 15878827.5946 | 146.3354 | 87.4873 | 25.349 | 32.23% | 34.75%
5 | 2.8 | Current | 25% | 75% | Improved | ASHP | No | 12496479.9628 | 1909158.7 | 14405638.6628 | 132.7588 | 57.752 | 22.9209 | 38.52% | 41%
5 | 2.8 | Improved | Current | None | Improved | ASHP | No | 13679403.8646 | 2481915.1 | 16161318.9646 | 148.9388 | 83.018 | 25.777 | 31.03% | 33.65%
5 | 2.8 | Improved | Current | 75% | Improved | ASHP | No | 12830658.9351 | 1863743.7 | 14694402.6351 | 135.42 | 53.0493 | 23.3649 | 37.29% | 39.86%
5 | 2.8 | Improved | 25% | None | Improved | ASHP | No | 13244351.9007 | 2523726.2 | 15768078.1007 | 145.3148 | 85.5892 | 25.1687 | 32.71% | 35.21%
5 | 2.8 | Improved | 25% | 75% | Improved | ASHP | No | 12418092.9693 | 1883433.3 | 14301526.2693 | 131.7994 | 55.7542 | 22.753 | 38.96% | 41.43%
5 | 4 | Current | Current | None | Improved | ASHP | No | 13486254.8806 | 2403332.5 | 15889587.3806 | 146.4346 | 77.7659 | 25.3368 | 32.19% | 34.78%
5 | 4 | Current | Current | 75% | Improved | ASHP | No | 12603050.9539 | 1768753.1 | 14371804.0539 | 132.447 | 47.0125 | 22.842 | 38.66% | 41.2%
5 | 4 | Current | 25% | None | Improved | ASHP | No | 13051810.9167 | 2429556 | 15481366.9167 | 142.6725 | 80.2417 | 24.7021 | 33.93% | 36.41%
5 | 4 | Current | 25% | 75% | Improved | ASHP | No | 12180356.989 | 1795972.8 | 13976329.789 | 128.8024 | 49.608 | 22.2274 | 40.35% | 42.78%
5 | 4 | Improved | Current | None | Improved | ASHP | No | 13416056.8865 | 2369930.5 | 15785987.3865 | 145.4798 | 75.8394 | 25.1684 | 32.63% | 35.21%
5 | 4 | Improved | Current | 75% | Improved | ASHP | No | 12528921.9601 | 1736904 | 14265825.9601 | 131.4704 | 45.0404 | 22.6701 | 39.12% | 41.64%
5 | 4 | Improved | 25% | None | Improved | ASHP | No | 12983109.9224 | 2398498 | 15381607.9224 | 141.7531 | 78.3048 | 24.5401 | 34.35% | 36.83%
5 | 4 | Improved | 25% | 75% | Improved | ASHP | No | 12103869.9954 | 1765207.8 | 13869077.7954 | 127.814 | 47.6015 | 22.0537 | 40.81% | 43.23%
5 | 5.5 | Current | Current | None | Improved | ASHP | No | 13356272.8914 | 2339341.3 | 15695614.1914 | 144.6469 | 74.1173 | 25.0212 | 33.01% | 35.59%
5 | 5.5 | Current | Current | 75% | Improved | ASHP | No | 12456566.9661 | 1708922.5 | 14165489.4661 | 130.5457 | 43.0328 | 22.5077 | 39.54% | 42.06%
5 | 5.5 | Current | 25% | None | Improved | ASHP | No | 12919089.9277 | 2365154.6 | 15284244.5277 | 140.8559 | 76.4867 | 24.3814 | 34.77% | 37.24%
5 | 5.5 | Current | 25% | 75% | Improved | ASHP | No | 12026932.0018 | 1732655.5 | 13759587.5018 | 126.805 | 45.5477 | 21.8762 | 41.28% | 43.69%
5 | 5.5 | Improved | Current | None | Improved | ASHP | No | 13274972.8982 | 2312561.1 | 15587533.9982 | 143.6509 | 72.0565 | 24.8469 | 33.48% | 36.04%
5 | 5.5 | Improved | Current | 75% | Improved | ASHP | No | 12382235.9723 | 1679476 | 14061711.9723 | 129.5893 | 41.0658 | 22.3397 | 39.99% | 42.5%
5 | 5.5 | Improved | 25% | None | Improved | ASHP | No | 12848473.9336 | 2335356.5 | 15183830.4336 | 139.9305 | 74.5938 | 24.2186 | 35.2% | 37.66%
5 | 5.5 | Improved | 25% | 75% | Improved | ASHP | No | 11950833.0081 | 1703384.8 | 13654217.8081 | 125.8339 | 43.5415 | 21.7057 | 41.73% | 44.13%
10 | 2.8 | Current | Current | None | Improved | ASHP | No | 13553195.8751 | 2442067.1 | 15995262.9751 | 147.4084 | 79.8531 | 25.5095 | 31.74% | 34.34%
10 | 2.8 | Current | Current | 75% | Improved | ASHP | No | 12684200.9472 | 1807546.3 | 14491747.2472 | 133.5524 | 49.3955 | 23.0371 | 38.15% | 40.7%
10 | 2.8 | Current | 25% | None | Improved | ASHP | No | 13120488.911 | 2467616.7 | 15588105.611 | 143.6562 | 82.3566 | 24.8764 | 33.47% | 35.97%
10 | 2.8 | Current | 25% | 75% | Improved | ASHP | No | 12267189.9818 | 1831337.9 | 14098527.8818 | 129.9286 | 52.0664 | 22.4254 | 39.83% | 42.27%
10 | 2.8 | Improved | Current | None | Improved | ASHP | No | 13480577.8811 | 2410921.2 | 15891499.0811 | 146.4522 | 77.9807 | 25.3412 | 32.18% | 34.77%
10 | 2.8 | Improved | Current | 75% | Improved | ASHP | No | 12606875.9536 | 1775902.3 | 14382778.2536 | 132.5482 | 47.4141 | 22.8605 | 38.62% | 41.15%
10 | 2.8 | Improved | 25% | None | Improved | ASHP | No | 13054619.9165 | 2432632.5 | 15487252.4165 | 142.7267 | 80.5621 | 24.7119 | 33.9% | 36.39%
10 | 2.8 | Improved | 25% | 75% | Improved | ASHP | No | 12187580.9884 | 1802272.3 | 13989853.2884 | 128.9271 | 50.0512 | 22.2498 | 40.29% | 42.73%
10 | 4 | Current | Current | None | Improved | ASHP | No | 13289598.897 | 2317190.5 | 15606789.397 | 143.8284 | 72.6384 | 24.8779 | 33.39% | 35.96%
10 | 4 | Current | Current | 75% | Improved | ASHP | No | 12384312.9721 | 1684603.5 | 14068916.4721 | 129.6557 | 41.4007 | 22.352 | 39.96% | 42.46%
10 | 4 | Current | 25% | None | Improved | ASHP | No | 12844270.9339 | 2341831.8 | 15186102.7339 | 139.9514 | 74.859 | 24.2234 | 35.19% | 37.65%
10 | 4 | Current | 25% | 75% | Improved | ASHP | No | 11955086.0077 | 1707897 | 13662983.0077 | 125.9147 | 43.9073 | 21.7203 | 41.69% | 44.09%
10 | 4 | Improved | Current | None | Improved | ASHP | No | 13211457.9034 | 2289677.8 | 15501135.7034 | 142.8547 | 70.6042 | 24.7073 | 33.84% | 36.4%
10 | 4 | Improved | Current | 75% | Improved | ASHP | No | 12307390.9785 | 1656329 | 13963719.9785 | 128.6862 | 39.4283 | 22.1819 | 40.41% | 42.9%
10 | 4 | Improved | 25% | None | Improved | ASHP | No | 12780702.9392 | 2314114 | 15094816.9392 | 139.1101 | 73.0681 | 24.0753 | 35.58% | 38.03%
10 | 4 | Improved | 25% | 75% | Improved | ASHP | No | 11878806.0141 | 1679593.2 | 13558399.2141 | 124.9509 | 41.8877 | 21.5512 | 42.14% | 44.52%
10 | 5.5 | Current | Current | None | Improved | ASHP | No | 13155056.9081 | 2253257.9 | 15408314.8081 | 141.9993 | 68.966 | 24.5552 | 34.24% | 36.79%
10 | 5.5 | Current | Current | 75% | Improved | ASHP | No | 12234396.9845 | 1626179.3 | 13860576.2845 | 127.7357 | 37.4599 | 22.0148 | 40.85% | 43.33%
10 | 5.5 | Current | 25% | None | Improved | ASHP | No | 12707492.9453 | 2279598.6 | 14987091.5453 | 138.1174 | 71.0988 | 23.9001 | 36.04% | 38.48%
10 | 5.5 | Current | 25% | 75% | Improved | ASHP | No | 11803970.0203 | 1650176 | 13454146.0203 | 123.9901 | 39.8544 | 21.3825 | 42.58% | 44.96%
10 | 5.5 | Improved | Current | None | Improved | ASHP | No | 13073608.9149 | 2227356.7 | 15300965.6149 | 141.01 | 66.8846 | 24.3822 | 34.7% | 37.24%
10 | 5.5 | Improved | Current | 75% | Improved | ASHP | No | 12160566.9907 | 1597260.2 | 13757827.1907 | 126.7888 | 35.5103 | 21.8485 | 41.28% | 43.76%
10 | 5.5 | Improved | 25% | None | Improved | ASHP | No | 12642842.9506 | 2251324.1 | 14894167.0506 | 137.261 | 69.3468 | 23.7493 | 36.44% | 38.87%
10 | 5.5 | Improved | 25% | 75% | Improved | ASHP | No | 11727031.0267 | 1620202.1 | 13347233.1267 | 123.0048 | 37.8437 | 21.2095 | 43.04% | 45.4%
15 | 2.8 | Current | Current | None | Improved | ASHP | No | 13492899.8801 | 2407668.9 | 15900568.7801 | 146.5358 | 78.2663 | 25.3548 | 32.14% | 34.73%
15 | 2.8 | Current | Current | 75% | Improved | ASHP | No | 12607473.9536 | 1775052.6 | 14382526.5536 | 132.5459 | 47.4586 | 22.86 | 38.62% | 41.16%
15 | 2.8 | Current | 25% | None | Improved | ASHP | No | 13050712.9168 | 2431460.5 | 15482173.4168 | 142.6799 | 80.5161 | 24.7037 | 33.93% | 36.41%
15 | 2.8 | Current | 25% | 75% | Improved | ASHP | No | 12188119.9884 | 1801627.7 | 13989747.6884 | 128.9261 | 50.1023 | 22.2495 | 40.29% | 42.73%
15 | 2.8 | Improved | Current | None | Improved | ASHP | No | 13422152.886 | 2377577.8 | 15799730.686 | 145.6065 | 76.4009 | 25.1913 | 32.57% | 35.15%
15 | 2.8 | Improved | Current | 75% | Improved | ASHP | No | 12529555.96 | 1748243.1 | 14277799.06 | 131.5807 | 45.4723 | 22.6909 | 39.07% | 41.59%
15 | 2.8 | Improved | 25% | None | Improved | ASHP | No | 12987354.922 | 2396417.7 | 15383772.622 | 141.7731 | 78.7461 | 24.5431 | 34.35% | 36.82%
15 | 2.8 | Improved | 25% | 75% | Improved | ASHP | No | 12109846.9949 | 1771331.5 | 13881178.4949 | 127.9255 | 48.0808 | 22.0738 | 40.76% | 43.18%
15 | 4 | Current | Current | None | Improved | ASHP | No | 13215793.9031 | 2288359.3 | 15504153.2031 | 142.8825 | 70.7529 | 24.7118 | 33.83% | 36.39%
15 | 4 | Current | Current | 75% | Improved | ASHP | No | 12306424.9786 | 1657149.4 | 13963574.3786 | 128.6849 | 39.4774 | 22.1819 | 40.41% | 42.9%
15 | 4 | Current | 25% | None | Improved | ASHP | No | 12780383.9392 | 2312033.7 | 15092417.6392 | 139.088 | 73.1491 | 24.0711 | 35.59% | 38.04%
15 | 4 | Current | 25% | 75% | Improved | ASHP | No | 11877654.0142 | 1680325.7 | 13557979.7142 | 124.947 | 41.9419 | 21.5507 | 42.14% | 44.53%
15 | 4 | Improved | Current | None | Improved | ASHP | No | 13147368.9088 | 2254840.1 | 15402209.0088 | 141.943 | 68.943 | 24.5459 | 34.27% | 36.82%
15 | 4 | Improved | Current | 75% | Improved | ASHP | No | 12230067.9849 | 1627380.6 | 13857448.5849 | 127.7069 | 37.5076 | 22.0101 | 40.86% | 43.34%
15 | 4 | Improved | 25% | None | Improved | ASHP | No | 12702498.9457 | 2283524.8 | 14986023.7457 | 138.1075 | 71.1678 | 23.8992 | 36.04% | 38.48%
15 | 4 | Improved | 25% | 75% | Improved | ASHP | No | 11801436.0205 | 1651435.9 | 13452871.9205 | 123.9784 | 39.9204 | 21.3807 | 42.59% | 44.96%
15 | 5.5 | Current | Current | None | Improved | ASHP | No | 13077216.9146 | 2228323.6 | 15305540.5146 | 141.0521 | 67.0149 | 24.3896 | 34.68% | 37.22%
15 | 5.5 | Current | Current | 75% | Improved | ASHP | No | 12158815.9908 | 1598959.6 | 13757775.5908 | 126.7883 | 35.5611 | 21.8487 | 41.28% | 43.76%
15 | 5.5 | Current | 25% | None | Improved | ASHP | No | 12644378.9505 | 2250708.8 | 14895087.7505 | 137.2695 | 69.3811 | 23.7507 | 36.43% | 38.86%
15 | 5.5 | Current | 25% | 75% | Improved | ASHP | No | 11725876.0268 | 1621462 | 13347338.0268 | 123.0058 | 37.8994 | 21.2098 | 43.04% | 45.4%
15 | 5.5 | Improved | Current | None | Improved | ASHP | No | 13013877.9198 | 2180593.9 | 15194471.8198 | 140.0285 | 65.2519 | 24.2068 | 35.15% | 37.69%
15 | 5.5 | Improved | Current | 75% | Improved | ASHP | No | 12083482.9971 | 1557675.9 | 13641158.8971 | 125.7136 | 33.6243 | 21.6584 | 41.78% | 44.25%
15 | 5.5 | Improved | 25% | None | Improved | ASHP | No | 12570956.9566 | 2219445.7 | 14790402.6566 | 136.3047 | 67.4651 | 23.5809 | 36.88% | 39.3%
15 | 5.5 | Improved | 25% | 75% | Improved | ASHP | No | 11649227.0331 | 1593128.9 | 13242355.9331 | 122.0383 | 35.8957 | 21.0402 | 43.48% | 45.84%
5 | 2.8 | Current | Current | None | Current | Current | Yes | 11627263.0183 | 11604177.1 | 23231440.1183 | 214.0953 | 100.9439 | 38.535 | 0.8536% | 0.8066%
5 | 2.8 | Current | Current | 75% | Current | Current | Yes | 11988437.9884 | 7677596.2 | 19666034.1884 | 181.2374 | 65.5869 | 32.2254 | 16.07% | 17.05%
5 | 2.8 | Current | 25% | None | Current | Current | Yes | 11103698.0618 | 11891141.3 | 22994839.3618 | 211.9148 | 103.6877 | 38.2172 | 1.863% | 1.625%
5 | 2.8 | Current | 25% | 75% | Current | Current | Yes | 11466316.0317 | 7972383.5 | 19438699.5317 | 179.1423 | 68.3266 | 31.9236 | 17.04% | 17.83%
5 | 2.8 | Improved | Current | None | Current | Current | Yes | 11628447.0182 | 11403970.2 | 23032417.2182 | 212.2611 | 98.9763 | 38.1863 | 1.703% | 1.704%
5 | 2.8 | Improved | Current | 75% | Current | Current | Yes | 11989692.9883 | 7470796.8 | 19460489.7883 | 179.3431 | 63.6202 | 31.8653 | 16.95% | 17.98%
5 | 2.8 | Improved | 25% | None | Current | Current | Yes | 11103910.0618 | 11684224.7 | 22788134.7618 | 210.0099 | 101.693 | 37.8553 | 2.745% | 2.556%
5 | 2.8 | Improved | 25% | 75% | Current | Current | Yes | 11466718.0317 | 7766375.2 | 19233093.2317 | 177.2475 | 66.3327 | 31.5635 | 17.92% | 18.75%
5 | 4 | Current | Current | None | Current | Current | Yes | 11640697.0172 | 10787908.4 | 22428605.4172 | 206.6965 | 92.9113 | 37.1268 | 4.28% | 4.432%
5 | 4 | Current | Current | 75% | Current | Current | Yes | 12001176.9873 | 6831881 | 18833057.9873 | 173.5609 | 57.5606 | 30.7646 | 19.62% | 20.81%
5 | 4 | Current | 25% | None | Current | Current | Yes | 11113475.061 | 11053923.1 | 22167398.161 | 204.2893 | 95.5177 | 36.7666 | 5.395% | 5.359%
5 | 4 | Current | 25% | 75% | Current | Current | Yes | 11476213.0309 | 7115885.9 | 18592098.9309 | 171.3402 | 60.1614 | 30.4394 | 20.65% | 21.65%
5 | 4 | Improved | Current | None | Current | Current | Yes | 11643899.017 | 10587906.6 | 22231805.617 | 204.8829 | 90.9407 | 36.7816 | 5.12% | 5.32%
5 | 4 | Improved | Current | 75% | Current | Current | Yes | 12004442.987 | 6622093 | 18626535.987 | 171.6576 | 55.5928 | 30.4023 | 20.51% | 21.74%
5 | 4 | Improved | 25% | None | Current | Current | Yes | 11115829.0608 | 10850551.8 | 21966380.8608 | 202.4368 | 93.5131 | 36.4142 | 6.253% | 6.266%
5 | 4 | Improved | 25% | 75% | Current | Current | Yes | 11478725.0307 | 6907445.7 | 18386170.7307 | 169.4425 | 58.1587 | 30.0784 | 21.53% | 22.57%
5 | 5.5 | Current | Current | None | Current | Current | Yes | 11650580.0164 | 10383832.1 | 22034412.1164 | 203.0638 | 88.9258 | 36.4347 | 5.962% | 6.213%
5 | 5.5 | Current | Current | 75% | Current | Current | Yes | 12010641.9865 | 6406679.4 | 18417321.3865 | 169.7295 | 53.5802 | 30.0349 | 21.4% | 22.69%
5 | 5.5 | Current | 25% | None | Current | Current | Yes | 11121347.0603 | 10642932 | 21764279.0603 | 200.5743 | 91.4476 | 36.0593 | 7.115% | 7.179%
5 | 5.5 | Current | 25% | 75% | Current | Current | Yes | 11483878.0302 | 6689688.1 | 18173566.1302 | 167.4831 | 56.0956 | 29.7051 | 22.44% | 23.54%
5 | 5.5 | Improved | Current | None | Current | Current | Yes | 11655250.016 | 10181164 | 21836414.016 | 201.2391 | 86.9612 | 36.0872 | 6.807% | 7.108%
5 | 5.5 | Improved | Current | 75% | Current | Current | Yes | 12015403.9861 | 6196276.1 | 18211680.0861 | 167.8344 | 51.6187 | 29.6739 | 22.28% | 23.62%
5 | 5.5 | Improved | 25% | None | Current | Current | Yes | 11124809.06 | 10440293.2 | 21565102.26 | 198.7387 | 89.444 | 35.7099 | 7.965% | 8.079%
5 | 5.5 | Improved | 25% | 75% | Current | Current | Yes | 11487454.0299 | 6475446.5 | 17962900.5299 | 165.5417 | 54.0943 | 29.3356 | 23.34% | 24.49%
10 | 2.8 | Current | Current | None | Current | Current | Yes | 11627896.0183 | 11032446.2 | 22660342.2183 | 208.8322 | 95.3042 | 37.5349 | 3.291% | 3.381%
10 | 2.8 | Current | Current | 75% | Current | Current | Yes | 11988284.9884 | 7085120.9 | 19073405.8884 | 175.7758 | 59.9494 | 31.1878 | 18.6% | 19.72%
10 | 2.8 | Current | 25% | None | Current | Current | Yes | 11102694.0619 | 11305375.7 | 22408069.7619 | 206.5073 | 97.9846 | 37.19 | 4.368% | 4.269%
10 | 2.8 | Current | 25% | 75% | Current | Current | Yes | 11465153.0318 | 7377417.7 | 18842570.7318 | 173.6485 | 62.6255 | 30.88 | 19.58% | 20.51%
10 | 2.8 | Improved | Current | None | Current | Current | Yes | 11629221.0182 | 10831125.9 | 22460346.9182 | 206.9891 | 93.3227 | 37.1845 | 4.144% | 4.283%
10 | 2.8 | Improved | Current | 75% | Current | Current | Yes | 11989950.9882 | 6877618.3 | 18867569.2882 | 173.8789 | 57.9699 | 30.8271 | 19.48% | 20.65%
10 | 2.8 | Improved | 25% | None | Current | Current | Yes | 11103518.0618 | 11102033.7 | 22205551.7618 | 204.6409 | 95.972 | 36.8352 | 5.232% | 5.182%
10 | 2.8 | Improved | 25% | 75% | Current | Current | Yes | 11466149.0317 | 7165871.7 | 18632020.7317 | 171.7081 | 60.6139 | 30.5112 | 20.48% | 21.46%
10 | 4 | Current | Current | None | Current | Current | Yes | 11643882.017 | 10219195.4 | 21863077.417 | 201.4848 | 87.2954 | 36.136 | 6.693% | 6.982%
10 | 4 | Current | Current | 75% | Current | Current | Yes | 12003733.9871 | 6233692.2 | 18237426.1871 | 168.0717 | 51.9506 | 29.7211 | 22.17% | 23.49%
10 | 4 | Current | 25% | None | Current | Current | Yes | 11115082.0608 | 10480434.2 | 21595516.2608 | 199.019 | 89.8088 | 35.7649 | 7.835% | 7.937%
10 | 4 | Current | 25% | 75% | Current | Current | Yes | 11477331.0308 | 6514386.2 | 17991717.2308 | 165.8073 | 54.4565 | 29.3879 | 23.22% | 24.35%
10 | 4 | Improved | Current | None | Current | Current | Yes | 11647414.0167 | 10014945.1 | 21662359.1167 | 199.635 | 85.3234 | 35.7839 | 7.55% | 7.888%
10 | 4 | Improved | Current | 75% | Current | Current | Yes | 12007715.9868 | 6019479.9 | 18027195.8868 | 166.1342 | 49.9821 | 29.3523 | 23.06% | 24.44%
10 | 4 | Improved | 25% | None | Current | Current | Yes | 11118717.0605 | 10273957.1 | 21392674.1605 | 197.1497 | 87.7911 | 35.4091 | 8.701% | 8.853%
10 | 4 | Improved | 25% | 75% | Current | Current | Yes | 11480923.0305 | 6299207 | 17780130.0305 | 163.8573 | 52.4417 | 29.0168 | 24.12% | 25.31%
10 | 5.5 | Current | Current | None | Current | Current | Yes | 11654763.0161 | 9816437.6 | 21471200.6161 | 197.8733 | 83.3502 | 35.4478 | 8.366% | 8.753%
10 | 5.5 | Current | Current | 75% | Current | Current | Yes | 12014169.9862 | 5805121.1 | 17819291.0862 | 164.2182 | 48.0133 | 28.9871 | 23.95% | 25.38%
10 | 5.5 | Current | 25% | None | Current | Current | Yes | 11125075.06 | 10065604.8 | 21190679.86 | 195.2881 | 85.7532 | 35.0542 | 9.563% | 9.767%
10 | 5.5 | Current | 25% | 75% | Current | Current | Yes | 11486581.03 | 6076292.6 | 17562873.63 | 161.8552 | 50.4073 | 28.6353 | 25.05% | 26.29%
10 | 5.5 | Improved | Current | None | Current | Current | Yes | 11659379.0157 | 9619951.8 | 21279330.8157 | 196.1051 | 81.4002 | 35.111 | 9.185% | 9.62%
10 | 5.5 | Improved | Current | 75% | Current | Current | Yes | 12018871.9858 | 5593868.1 | 17612740.0858 | 162.3147 | 46.0679 | 28.6245 | 24.83% | 26.32%
10 | 5.5 | Improved | 25% | None | Current | Current | Yes | 11129175.0597 | 9861032.2 | 20990207.2597 | 193.4406 | 83.7435 | 34.7024 | 10.42% | 10.67%
10 | 5.5 | Improved | 25% | 75% | Current | Current | Yes | 11490789.0297 | 5857275.1 | 17348064.1297 | 159.8755 | 48.4007 | 28.2584 | 25.96% | 27.26%
15 | 2.8 | Current | Current | None | Current | Current | Yes | 11627622.0183 | 10836487.8 | 22464109.8183 | 207.0237 | 93.3625 | 37.1914 | 4.128% | 4.265%
15 | 2.8 | Current | Current | 75% | Current | Current | Yes | 11987754.9884 | 6880929.2 | 18868684.1884 | 173.8892 | 58.0092 | 30.8294 | 19.47% | 20.64%
15 | 2.8 | Current | 25% | None | Current | Current | Yes | 11102525.0619 | 11108567.6 | 22211092.6619 | 204.692 | 96.0175 | 36.8451 | 5.208% | 5.157%
15 | 2.8 | Current | 25% | 75% | Current | Current | Yes | 11464716.0318 | 7172317.7 | 18637033.7318 | 171.7543 | 60.6592 | 30.5202 | 20.46% | 21.44%
15 | 2.8 | Improved | Current | None | Current | Current | Yes | 11629752.0181 | 10637130.6 | 22266882.6181 | 205.2061 | 91.3767 | 36.8456 | 4.97% | 5.155%
15 | 2.8 | Improved | Current | 75% | Current | Current | Yes | 11990153.9882 | 6669266 | 18659419.9882 | 171.9607 | 56.0256 | 30.4626 | 20.37% | 21.59%
15 | 2.8 | Improved | 25% | None | Current | Current | Yes | 11103836.0618 | 10905723.7 | 22009559.7618 | 202.8347 | 93.9973 | 36.492 | 6.068% | 6.066%
15 | 2.8 | Improved | 25% | 75% | Current | Current | Yes | 11466154.0317 | 6960068.5 | 18426222.5317 | 169.8116 | 58.6404 | 30.1508 | 21.36% | 22.39%
15 | 4 | Current | Current | None | Current | Current | Yes | 11644499.0169 | 10020453.5 | 21664952.5169 | 199.6589 | 85.3711 | 35.7889 | 7.539% | 7.875%
15 | 4 | Current | Current | 75% | Current | Current | Yes | 12004400.987 | 6024285.1 | 18028686.087 | 166.148 | 50.0292 | 29.3555 | 23.06% | 24.44%
15 | 4 | Current | 25% | None | Current | Current | Yes | 11116126.0608 | 10280608.2 | 21396734.2608 | 197.1871 | 87.8434 | 35.4167 | 8.684% | 8.834%
15 | 4 | Current | 25% | 75% | Current | Current | Yes | 11477995.0307 | 6304100.1 | 17782095.1307 | 163.8754 | 52.4929 | 29.0208 | 24.11% | 25.3%
15 | 4 | Improved | Current | None | Current | Current | Yes | 11648761.0166 | 9821067 | 21469828.0166 | 197.8607 | 83.4013 | 35.4465 | 8.372% | 8.757%
15 | 4 | Improved | Current | 75% | Current | Current | Yes | 12008485.9867 | 5810893.2 | 17819379.1867 | 164.219 | 48.0634 | 28.9883 | 23.95% | 25.38%
15 | 4 | Improved | 25% | None | Current | Current | Yes | 11119665.0605 | 10072812.6 | 21192477.6605 | 195.3047 | 85.8236 | 35.0584 | 9.555% | 9.756%
15 | 4 | Improved | 25% | 75% | Current | Current | Yes | 11481627.0304 | 6084438 | 17566065.0304 | 161.8846 | 50.4765 | 28.6418 | 25.03% | 26.27%
15 | 5.5 | Current | Current | None | Current | Current | Yes | 11655584.016 | 9625284.4 | 21280868.416 | 196.1193 | 81.4506 | 35.1144 | 9.178% | 9.612%
15 | 5.5 | Current | Current | 75% | Current | Current | Yes | 12014936.9862 | 5598087.3 | 17613024.2862 | 162.3173 | 46.1171 | 28.6258 | 24.83% | 26.31%
15 | 5.5 | Current | 25% | None | Current | Current | Yes | 11126194.0599 | 9867361 | 20993555.0599 | 193.4715 | 83.7981 | 34.7089 | 10.4% | 10.66%
15 | 5.5 | Current | 25% | 75% | Current | Current | Yes | 11487454.0299 | 5863047.2 | 17350501.2299 | 159.898 | 48.4542 | 28.2633 | 25.95% | 27.25%
15 | 5.5 | Improved | Current | None | Current | Current | Yes | 11656234.0159 | 9400524.1 | 21056758.1159 | 194.0539 | 79.5074 | 34.7218 | 10.13% | 10.62%
15 | 5.5 | Improved | Current | 75% | Current | Current | Yes | 12015402.9861 | 5359995.5 | 17375398.4861 | 160.1274 | 44.1801 | 28.2096 | 25.85% | 27.39%
15 | 5.5 | Improved | 25% | None | Current | Current | Yes | 11130349.0596 | 9667447.1 | 20797796.1596 | 191.6674 | 81.7918 | 34.3653 | 11.24% | 11.54%
15 | 5.5 | Improved | 25% | 75% | Current | Current | Yes | 11491584.0296 | 5645582.6 | 17137166.6296 | 157.9319 | 46.4526 | 27.889 | 26.86% | 28.21%
5 | 2.8 | Current | Current | None | Improved | Current | Yes | 10460237.1152 | 9782303.1 | 20242540.2152 | 186.5503 | 86.9803 | 33.5166 | 13.61% | 13.72%
5 | 2.8 | Current | Current | 75% | Improved | Current | Yes | 10795001.0874 | 6274360.6 | 17069361.6874 | 157.3071 | 54.992 | 27.8987 | 27.15% | 28.19%
5 | 2.8 | Current | 25% | None | Improved | Current | Yes | 9934728.1588 | 10069355.2 | 20004083.3588 | 184.3527 | 89.724 | 33.1959 | 14.63% | 14.55%
5 | 2.8 | Current | 25% | 75% | Improved | Current | Yes | 10269821.131 | 6568122.4 | 16837943.531 | 155.1744 | 57.7317 | 27.5902 | 28.14% | 28.98%
5 | 2.8 | Improved | Current | None | Improved | Current | Yes | 10460853.1151 | 9582096.2 | 20042949.3151 | 184.7109 | 85.0128 | 33.167 | 14.46% | 14.62%
5 | 2.8 | Improved | Current | 75% | Improved | Current | Yes | 10796120.0873 | 6066887.3 | 16863007.3873 | 155.4054 | 53.0252 | 27.5371 | 28.03% | 29.12%
5 | 2.8 | Improved | 25% | None | Improved | Current | Yes | 9934184.1589 | 9862907.4 | 19797091.5589 | 182.4452 | 87.7294 | 32.8336 | 15.51% | 15.48%
5 | 2.8 | Improved | 25% | 75% | Improved | Current | Yes | 10270035.131 | 6362641.5 | 16632676.631 | 153.2827 | 55.7377 | 27.2308 | 29.02% | 29.9%
5 | 4 | Current | Current | None | Improved | Current | Yes | 10472324.1142 | 8965096.8 | 19437420.9142 | 179.1305 | 78.9477 | 32.1046 | 17.05% | 17.36%
5 | 4 | Current | Current | 75% | Improved | Current | Yes | 10808202.0863 | 5428059.4 | 16236261.4863 | 149.6294 | 46.9655 | 26.4375 | 30.71% | 31.95%
5 | 4 | Current | 25% | None | Improved | Current | Yes | 9943109.1581 | 9231375.2 | 19174484.3581 | 176.7074 | 81.5542 | 31.7417 | 18.17% | 18.29%
5 | 4 | Current | 25% | 75% | Improved | Current | Yes | 10279977.1302 | 5712591.7 | 15992568.8302 | 147.3836 | 49.5665 | 26.1081 | 31.75% | 32.79%
5 | 4 | Improved | Current | None | Improved | Current | Yes | 10475007.114 | 8765475.9 | 19240483.014 | 177.3156 | 76.9771 | 31.7593 | 17.89% | 18.25%
5 | 4 | Improved | Current | 75% | Improved | Current | Yes | 10810967.0861 | 5218154.2 | 16029121.2861 | 147.7205 | 44.9978 | 26.0743 | 31.59% | 32.88%
5 | 4 | Improved | 25% | None | Improved | Current | Yes | 9944736.158 | 9027652.3 | 18972388.458 | 174.8449 | 79.5496 | 31.3876 | 19.03% | 19.2%
5 | 4 | Improved | 25% | 75% | Improved | Current | Yes | 10282204.13 | 5504122.2 | 15786326.33 | 145.4829 | 47.5637 | 25.7466 | 32.63% | 33.73%
5 | 5.5 | Current | Current | None | Improved | Current | Yes | 10481454.1134 | 8560581 | 19042035.1134 | 175.4867 | 74.9621 | 31.4106 | 18.73% | 19.15%
5 | 5.5 | Current | Current | 75% | Improved | Current | Yes | 10817349.0856 | 5002389 | 15819738.0856 | 145.7908 | 42.9852 | 25.7065 | 32.48% | 33.83%
5 | 5.5 | Current | 25% | None | Improved | Current | Yes | 9949898.1576 | 8819768.8 | 18769666.9576 | 172.9767 | 77.4841 | 31.0316 | 19.9% | 20.12%
5 | 5.5 | Current | 25% | 75% | Improved | Current | Yes | 10287556.1295 | 5285339.1 | 15572895.2295 | 143.516 | 45.5006 | 25.3719 | 33.54% | 34.69%
5 | 5.5 | Improved | Current | None | Improved | Current | Yes | 10485484.1131 | 8358498.9 | 18843983.0131 | 173.6615 | 72.9975 | 31.0631 | 19.58% | 20.04%
5 | 5.5 | Improved | Current | 75% | Improved | Current | Yes | 10821634.0852 | 4791839.2 | 15613473.2852 | 143.89 | 41.0238 | 25.3445 | 33.37% | 34.76%
5 | 5.5 | Improved | 25% | None | Improved | Current | Yes | 9952629.1573 | 8617305.8 | 18569934.9573 | 171.136 | 75.4804 | 30.6814 | 20.75% | 21.02%
5 | 5.5 | Improved | 25% | 75% | Improved | Current | Yes | 10290660.1293 | 5071390.5 | 15362050.6293 | 141.5729 | 43.4992 | 25.0021 | 34.44% | 35.64%
10 | 2.8 | Current | Current | None | Improved | Current | Yes | 10460402.1152 | 9210103.4 | 19670505.5152 | 181.2786 | 81.3405 | 32.5149 | 16.05% | 16.3%
10 | 2.8 | Current | Current | 75% | Improved | Current | Yes | 10795727.0874 | 5681182.1 | 16476909.1874 | 151.8472 | 49.3545 | 26.8611 | 29.68% | 30.86%
10 | 2.8 | Current | 25% | None | Improved | Current | Yes | 9933436.1589 | 9483238 | 19416674.1589 | 178.9393 | 84.0211 | 32.1676 | 17.13% | 17.2%
10 | 2.8 | Current | 25% | 75% | Improved | Current | Yes | 10269293.131 | 5974797.4 | 16244090.531 | 149.7016 | 52.0305 | 26.5505 | 30.67% | 31.66%
10 | 2.8 | Improved | Current | None | Improved | Current | Yes | 10460985.1151 | 9008871 | 19469856.1151 | 179.4294 | 79.3591 | 32.1635 | 16.91% | 17.21%
10 | 2.8 | Improved | Current | 75% | Improved | Current | Yes | 10797008.0872 | 5473708.8 | 16270716.8872 | 149.947 | 47.3749 | 26.4999 | 30.56% | 31.79%
10 | 2.8 | Improved | 25% | None | Improved | Current | Yes | 9933507.1589 | 9279866.7 | 19213373.8589 | 177.0658 | 82.0082 | 31.8116 | 18% | 18.11%
10 | 2.8 | Improved | 25% | 75% | Improved | Current | Yes | 10270059.131 | 5762548.2 | 16032607.331 | 147.7526 | 50.0189 | 26.1801 | 31.58% | 32.61%
10 | 4 | Current | Current | None | Improved | Current | Yes | 10475214.114 | 8395651.3 | 18870865.414 | 173.9093 | 73.3319 | 31.112 | 19.46% | 19.91%
10 | 4 | Current | Current | 75% | Improved | Current | Yes | 10810966.0861 | 4829636.2 | 15640602.2861 | 144.14 | 41.3556 | 25.394 | 33.25% | 34.63%
10 | 4 | Current | 25% | None | Improved | Current | Yes | 9943797.1581 | 8657974.2 | 18601771.3581 | 171.4294 | 75.8453 | 30.7388 | 20.61% | 20.87%
10 | 4 | Current | 25% | 75% | Improved | Current | Yes | 10281655.13 | 5111033.4 | 15392688.53 | 141.8553 | 43.8616 | 25.0574 | 34.31% | 35.5%
10 | 4 | Improved | Current | None | Improved | Current | Yes | 10477974.1137 | 8192045.6 | 18670019.7137 | 172.0583 | 71.3597 | 30.7598 | 20.32% | 20.82%
10 | 4 | Improved | Current | 75% | Improved | Current | Yes | 10814378.0858 | 4615570.4 | 15429948.4858 | 142.1986 | 39.3871 | 25.0245 | 34.15% | 35.58%
10 | 4 | Improved | 25% | None | Improved | Current | Yes | 9946765.1578 | 8450764.6 | 18397529.7578 | 169.5471 | 73.8273 | 30.3806 | 21.48% | 21.8%
10 | 4 | Improved | 25% | 75% | Improved | Current | Yes | 10284708.1298 | 4895180.3 | 15179888.4298 | 139.8941 | 41.8467 | 24.6843 | 35.22% | 36.46%
10 | 5.5 | Current | Current | None | Improved | Current | Yes | 10484864.1132 | 7992981.4 | 18477845.5132 | 170.2873 | 69.3864 | 30.4221 | 21.14% | 21.69%
10 | 5.5 | Current | Current | 75% | Improved | Current | Yes | 10820808.0853 | 4399570.8 | 15220378.8853 | 140.2673 | 37.4182 | 24.6563 | 35.04% | 36.53%
10 | 5.5 | Current | 25% | None | Improved | Current | Yes | 9952323.1574 | 8243437.8 | 18195760.9574 | 167.6877 | 71.7897 | 30.0263 | 22.34% | 22.71%
10 | 5.5 | Current | 25% | 75% | Improved | Current | Yes | 10290420.1293 | 4672441.7 | 14962861.8293 | 137.8941 | 39.8123 | 24.3032 | 36.14% | 37.44%
10 | 5.5 | Improved | Current | None | Improved | Current | Yes | 10488462.1129 | 7796642.1 | 18285104.2129 | 168.5111 | 67.4362 | 30.0839 | 21.96% | 22.56%
10 | 5.5 | Improved | Current | 75% | Improved | Current | Yes | 10824682.085 | 4189138.2 | 15013820.285 | 138.3637 | 35.4729 | 24.294 | 35.92% | 37.46%
10 | 5.5 | Improved | 25% | None | Improved | Current | Yes | 9955589.1571 | 8037927.6 | 17993516.7571 | 165.8239 | 69.7798 | 29.6716 | 23.21% | 23.62%
10 | 5.5 | Improved | 25% | 75% | Improved | Current | Yes | 10294016.129 | 4453307 | 14747323.129 | 135.9077 | 37.8056 | 23.9251 | 37.06% | 38.41%
15 | 2.8 | Current | Current | None | Improved | Current | Yes | 10459793.1152 | 9013881.3 | 19473674.4152 | 179.4646 | 79.3989 | 32.1704 | 16.89% | 17.19%
15 | 2.8 | Current | Current | 75% | Improved | Current | Yes | 10795452.0874 | 5477664.3 | 16273116.3874 | 149.9691 | 47.4141 | 26.5044 | 30.55% | 31.77%
15 | 2.8 | Current | 25% | None | Improved | Current | Yes | 9932920.159 | 9286224.8 | 19219144.959 | 177.1189 | 82.0538 | 31.8218 | 17.98% | 18.09%
15 | 2.8 | Current | 25% | 75% | Improved | Current | Yes | 10269094.1311 | 5769170 | 16038264.1311 | 147.8047 | 50.0642 | 26.1901 | 31.55% | 32.58%
15 | 2.8 | Improved | Current | None | Improved | Current | Yes | 10461362.1151 | 8813586.5 | 19274948.6151 | 177.6332 | 77.4131 | 31.8221 | 17.74% | 18.09%
15 | 2.8 | Improved | Current | 75% | Improved | Current | Yes | 10797347.0872 | 5265122.1 | 16062469.1872 | 148.0278 | 45.4306 | 26.1352 | 31.45% | 32.73%
15 | 2.8 | Improved | 25% | None | Improved | Current | Yes | 9933481.1589 | 9082414 | 19015895.1589 | 175.2458 | 80.0337 | 31.4658 | 18.84% | 19%
15 | 2.8 | Improved | 25% | 75% | Improved | Current | Yes | 10270291.131 | 5556715.7 | 15827006.831 | 145.8578 | 48.0455 | 25.82 | 32.45% | 33.54%
15 | 4 | Current | Current | None | Improved | Current | Yes | 10475472.1139 | 8196938.7 | 18672410.8139 | 172.0804 | 71.4076 | 30.7645 | 20.31% | 20.81%
15 | 4 | Current | Current | 75% | Improved | Current | Yes | 10811607.086 | 4619467.3 | 15431074.386 | 142.209 | 39.4342 | 25.027 | 34.14% | 35.58%
15 | 4 | Current | 25% | None | Improved | Current | Yes | 9944369.158 | 8457679.4 | 18402048.558 | 169.5888 | 73.8798 | 30.389 | 21.46% | 21.78%
15 | 4 | Current | 25% | 75% | Improved | Current | Yes | 10282420.13 | 4900454.3 | 15182874.43 | 139.9217 | 41.898 | 24.6899 | 35.2% | 36.45%
15 | 4 | Improved | Current | None | Improved | Current | Yes | 10478756.1137 | 7997991.7 | 18476747.8137 | 170.2772 | 69.4375 | 30.4213 | 21.15% | 21.69%
15 | 4 | Improved | Current | 75% | Improved | Current | Yes | 10815084.0857 | 4406192.6 | 15221276.6857 | 140.2756 | 37.4684 | 24.659 | 35.04% | 36.53%
15 | 4 | Improved | 25% | None | Improved | Current | Yes | 9947061.1578 | 8250557.7 | 18197618.8578 | 167.7048 | 71.8598 | 30.0305 | 22.34% | 22.7%
15 | 4 | Improved | 25% | 75% | Improved | Current | Yes | 10285427.1297 | 4680440.6 | 14965867.7297 | 137.9218 | 39.8815 | 24.3094 | 36.13% | 37.42%
15 | 5.5 | Current | Current | None | Improved | Current | Yes | 10485236.1131 | 7801623.1 | 18286859.2131 | 168.5272 | 67.4867 | 30.0876 | 21.96% | 22.55%
15 | 5.5 | Current | Current | 75% | Improved | Current | Yes | 10821309.0852 | 4193474.6 | 15014783.6852 | 138.3726 | 35.5221 | 24.2963 | 35.92% | 37.46%
15 | 5.5 | Current | 25% | None | Improved | Current | Yes | 9953044.1573 | 8044490.8 | 17997534.9573 | 165.8609 | 69.8343 | 29.6791 | 23.19% | 23.6%
15 | 5.5 | Current | 25% | 75% | Improved | Current | Yes | 10291290.1292 | 4459489.3 | 14750779.4292 | 135.9396 | 37.8592 | 23.9317 | 37.05% | 38.4%
15 | 5.5 | Improved | Current | None | Improved | Current | Yes | 10483991.1132 | 7595175.3 | 18079166.4132 | 166.6132 | 65.5459 | 29.7241 | 22.84% | 23.49%
15 | 5.5 | Improved | Current | 75% | Improved | Current | Yes | 10820493.0853 | 3973197.2 | 14793690.2853 | 136.335 | 33.5874 | 23.9093 | 36.86% | 38.45%
15 | 5.5 | Improved | 25% | None | Improved | Current | Yes | 9956071.157 | 7843932.3 | 17800003.457 | 164.0405 | 67.828 | 29.3326 | 24.03% | 24.49%
15 | 5.5 | Improved | 25% | 75% | Improved | Current | Yes | 10294565.129 | 4241995.4 | 14536560.529 | 133.9654 | 35.8576 | 23.556 | 37.96% | 39.36%
5 | 2.8 | Current | Current | None | Improved | ASHP | Yes | 13544396.8592 | 2526392.5 | 16070789.3592 | 148.1045 | 84.825 | 25.6434 | 31.41% | 33.99%
5 | 2.8 | Current | Current | 75% | Improved | ASHP | Yes | 12709240.9285 | 1888326.4 | 14597567.3285 | 134.5276 | 55.0185 | 23.2177 | 37.7% | 40.23%
5 | 2.8 | Current | 25% | None | Improved | ASHP | Yes | 13118036.8946 | 2560790.7 | 15678827.5946 | 144.4922 | 87.4873 | 25.0357 | 33.09% | 35.56%
5 | 2.8 | Current | 25% | 75% | Improved | ASHP | Yes | 12296479.9628 | 1909158.7 | 14205638.6628 | 130.9157 | 57.752 | 22.6076 | 39.37% | 41.81%
5 | 2.8 | Improved | Current | None | Improved | ASHP | Yes | 13479403.8646 | 2481915.1 | 15961318.9646 | 147.0956 | 83.018 | 25.4637 | 31.88% | 34.45%
5 | 2.8 | Improved | Current | 75% | Improved | ASHP | Yes | 12630658.9351 | 1863743.7 | 14494402.6351 | 133.5769 | 53.0493 | 23.0516 | 38.14% | 40.66%
5 | 2.8 | Improved | 25% | None | Improved | ASHP | Yes | 13044351.9007 | 2523726.2 | 15568078.1007 | 143.4716 | 85.5892 | 24.8553 | 33.56% | 36.02%
5 | 2.8 | Improved | 25% | 75% | Improved | ASHP | Yes | 12218092.9693 | 1883433.3 | 14101526.2693 | 129.9562 | 55.7542 | 22.4397 | 39.82% | 42.24%
5 | 4 | Current | Current | None | Improved | ASHP | Yes | 13286254.8806 | 2403332.5 | 15689587.3806 | 144.5914 | 77.7659 | 25.0235 | 33.04% | 35.59%
5 | 4 | Current | Current | 75% | Improved | ASHP | Yes | 12403050.9539 | 1768753.1 | 14171804.0539 | 130.6039 | 47.0125 | 22.5287 | 39.52% | 42.01%
5 | 4 | Current | 25% | None | Improved | ASHP | Yes | 12851810.9167 | 2429556 | 15281366.9167 | 140.8293 | 80.2417 | 24.3888 | 34.78% | 37.22%
5 | 4 | Current | 25% | 75% | Improved | ASHP | Yes | 11980356.989 | 1795972.8 | 13776329.789 | 126.9593 | 49.608 | 21.9141 | 41.21% | 43.59%
5 | 4 | Improved | Current | None | Improved | ASHP | Yes | 13216056.8865 | 2369930.5 | 15585987.3865 | 143.6367 | 75.8394 | 24.855 | 33.48% | 36.02%
5 | 4 | Improved | Current | 75% | Improved | ASHP | Yes | 12328921.9601 | 1736904 | 14065825.9601 | 129.6272 | 45.0404 | 22.3568 | 39.97% | 42.45%
5 | 4 | Improved | 25% | None | Improved | ASHP | Yes | 12783109.9224 | 2398498 | 15181607.9224 | 139.91 | 78.3048 | 24.2268 | 35.21% | 37.64%
5 | 4 | Improved | 25% | 75% | Improved | ASHP | Yes | 11903869.9954 | 1765207.8 | 13669077.7954 | 125.9709 | 47.6015 | 21.7404 | 41.66% | 44.04%
5 | 5.5 | Current | Current | None | Improved | ASHP | Yes | 13156272.8914 | 2339341.3 | 15495614.1914 | 142.8038 | 74.1173 | 24.7078 | 33.87% | 36.4%
5 | 5.5 | Current | Current | 75% | Improved | ASHP | Yes | 12256566.9661 | 1708922.5 | 13965489.4661 | 128.7025 | 43.0328 | 22.1944 | 40.4% | 42.87%
5 | 5.5 | Current | 25% | None | Improved | ASHP | Yes | 12719089.9277 | 2365154.6 | 15084244.5277 | 139.0127 | 76.4867 | 24.0681 | 35.62% | 38.05%
5 | 5.5 | Current | 25% | 75% | Improved | ASHP | Yes | 11826932.0018 | 1732655.5 | 13559587.5018 | 124.9618 | 45.5477 | 21.5629 | 42.13% | 44.49%
5 | 5.5 | Improved | Current | None | Improved | ASHP | Yes | 13074972.8982 | 2312561.1 | 15387533.9982 | 141.8078 | 72.0565 | 24.5336 | 34.33% | 36.85%
5 | 5.5 | Improved | Current | 75% | Improved | ASHP | Yes | 12182235.9723 | 1679476 | 13861711.9723 | 127.7462 | 41.0658 | 22.0264 | 40.84% | 43.3%
5 | 5.5 | Improved | 25% | None | Improved | ASHP | Yes | 12648473.9336 | 2335356.5 | 14983830.4336 | 138.0873 | 74.5938 | 23.9053 | 36.05% | 38.47%
5 | 5.5 | Improved | 25% | 75% | Improved | ASHP | Yes | 11750833.0081 | 1703384.8 | 13454217.8081 | 123.9908 | 43.5415 | 21.3924 | 42.58% | 44.93%
10 | 2.8 | Current | Current | None | Improved | ASHP | Yes | 13353195.8751 | 2442067.1 | 15795262.9751 | 145.5653 | 79.8531 | 25.1962 | 32.59% | 35.14%
10 | 2.8 | Current | Current | 75% | Improved | ASHP | Yes | 12484200.9472 | 1807546.3 | 14291747.2472 | 131.7093 | 49.3955 | 22.7237 | 39.01% | 41.51%
10 | 2.8 | Current | 25% | None | Improved | ASHP | Yes | 12920488.911 | 2467616.7 | 15388105.611 | 141.813 | 82.3566 | 24.563 | 34.33% | 36.77%
10 | 2.8 | Current | 25% | 75% | Improved | ASHP | Yes | 12067189.9818 | 1831337.9 | 13898527.8818 | 128.0854 | 52.0664 | 22.1121 | 40.68% | 43.08%
10 | 2.8 | Improved | Current | None | Improved | ASHP | Yes | 13280577.8811 | 2410921.2 | 15691499.0811 | 144.609 | 77.9807 | 25.0279 | 33.03% | 35.58%
10 | 2.8 | Improved | Current | 75% | Improved | ASHP | Yes | 12406875.9536 | 1775902.3 | 14182778.2536 | 130.705 | 47.4141 | 22.5472 | 39.47% | 41.96%
10 | 2.8 | Improved | 25% | None | Improved | ASHP | Yes | 12854619.9165 | 2432632.5 | 15287252.4165 | 140.8836 | 80.5621 | 24.3986 | 34.76% | 37.2%
10 | 2.8 | Improved | 25% | 75% | Improved | ASHP | Yes | 11987580.9884 | 1802272.3 | 13789853.2884 | 127.0839 | 50.0512 | 21.9365 | 41.15% | 43.53%
10 | 4 | Current | Current | None | Improved | ASHP | Yes | 13089598.897 | 2317190.5 | 15406789.397 | 141.9852 | 72.6384 | 24.5646 | 34.25% | 36.77%
10 | 4 | Current | Current | 75% | Improved | ASHP | Yes | 12184312.9721 | 1684603.5 | 13868916.4721 | 127.8125 | 41.4007 | 22.0386 | 40.81% | 43.27%
10 | 4 | Current | 25% | None | Improved | ASHP | Yes | 12644270.9339 | 2341831.8 | 14986102.7339 | 138.1083 | 74.859 | 23.91 | 36.04% | 38.45%
10 | 4 | Current | 25% | 75% | Improved | ASHP | Yes | 11755086.0077 | 1707897 | 13462983.0077 | 124.0716 | 43.9073 | 21.407 | 42.54% | 44.9%
10 | 4 | Improved | Current | None | Improved | ASHP | Yes | 13011457.9034 | 2289677.8 | 15301135.7034 | 141.0115 | 70.6042 | 24.394 | 34.7% | 37.21%
10 | 4 | Improved | Current | 75% | Improved | ASHP | Yes | 12107390.9785 | 1656329 | 13763719.9785 | 126.8431 | 39.4283 | 21.8686 | 41.26% | 43.71%
10 | 4 | Improved | 25% | None | Improved | ASHP | Yes | 12580702.9392 | 2314114 | 14894816.9392 | 137.267 | 73.0681 | 23.7619 | 36.43% | 38.83%
10 | 4 | Improved | 25% | 75% | Improved | ASHP | Yes | 11678806.0141 | 1679593.2 | 13358399.2141 | 123.1077 | 41.8877 | 21.2379 | 42.99% | 45.33%
10 | 5.5 | Current | Current | None | Improved | ASHP | Yes | 12955056.9081 | 2253257.9 | 15208314.8081 | 140.1561 | 68.966 | 24.2418 | 35.09% | 37.6%
10 | 5.5 | Current | Current | 75% | Improved | ASHP | Yes | 12034396.9845 | 1626179.3 | 13660576.2845 | 125.8925 | 37.4599 | 21.7015 | 41.7% | 44.14%
10 | 5.5 | Current | 25% | None | Improved | ASHP | Yes | 12507492.9453 | 2279598.6 | 14787091.5453 | 136.2742 | 71.0988 | 23.5868 | 36.89% | 39.28%
10 | 5.5 | Current | 25% | 75% | Improved | ASHP | Yes | 11603970.0203 | 1650176 | 13254146.0203 | 122.147 | 39.8544 | 21.0691 | 43.43% | 45.77%
10 | 5.5 | Improved | Current | None | Improved | ASHP | Yes | 12873608.9149 | 2227356.7 | 15100965.6149 | 139.1668 | 66.8846 | 24.0689 | 35.55% | 38.04%
10 | 5.5 | Improved | Current | 75% | Improved | ASHP | Yes | 11960566.9907 | 1597260.2 | 13557827.1907 | 124.9456 | 35.5103 | 21.5352 | 42.14% | 44.57%
10 | 5.5 | Improved | 25% | None | Improved | ASHP | Yes | 12442842.9506 | 2251324.1 | 14694167.0506 | 135.4179 | 69.3468 | 23.436 | 37.29% | 39.67%
10 | 5.5 | Improved | 25% | 75% | Improved | ASHP | Yes | 11527031.0267 | 1620202.1 | 13147233.1267 | 121.1617 | 37.8437 | 20.8961 | 43.89% | 46.21%
15 | 2.8 | Current | Current | None | Improved | ASHP | Yes | 13292899.8801 | 2407668.9 | 15700568.7801 | 144.6926 | 78.2663 | 25.0415 | 32.99% | 35.54%
15 | 2.8 | Current | Current | 75% | Improved | ASHP | Yes | 12407473.9536 | 1775052.6 | 14182526.5536 | 130.7027 | 47.4586 | 22.5466 | 39.47% | 41.96%
15 | 2.8 | Current | 25% | None | Improved | ASHP | Yes | 12850712.9168 | 2431460.5 | 15282173.4168 | 140.8368 | 80.5161 | 24.3904 | 34.78% | 37.22%
15 | 2.8 | Current | 25% | 75% | Improved | ASHP | Yes | 11988119.9884 | 1801627.7 | 13789747.6884 | 127.0829 | 50.1023 | 21.9362 | 41.15% | 43.53%
15 | 2.8 | Improved | Current | None | Improved | ASHP | Yes | 13222152.886 | 2377577.8 | 15599730.686 | 143.7633 | 76.4009 | 24.878 | 33.42% | 35.96%
15 | 2.8 | Improved | Current | 75% | Improved | ASHP | Yes | 12329555.96 | 1748243.1 | 14077799.06 | 129.7376 | 45.4723 | 22.3776 | 39.92% | 42.4%
15 | 2.8 | Improved | 25% | None | Improved | ASHP | Yes | 12787354.922 | 2396417.7 | 15183772.622 | 139.9299 | 78.7461 | 24.2298 | 35.2% | 37.63%
15 | 2.8 | Improved | 25% | 75% | Improved | ASHP | Yes | 11909846.9949 | 1771331.5 | 13681178.4949 | 126.0824 | 48.0808 | 21.7605 | 41.61% | 43.99%
15 | 4 | Current | Current | None | Improved | ASHP | Yes | 13015793.9031 | 2288359.3 | 15304153.2031 | 141.0393 | 70.7529 | 24.3985 | 34.69% | 37.2%
15 | 4 | Current | Current | 75% | Improved | ASHP | Yes | 12106424.9786 | 1657149.4 | 13763574.3786 | 126.8417 | 39.4774 | 21.8685 | 41.26% | 43.71%
15 | 4 | Current | 25% | None | Improved | ASHP | Yes | 12580383.9392 | 2312033.7 | 14892417.6392 | 137.2449 | 73.1491 | 23.7578 | 36.44% | 38.84%
15 | 4 | Current | 25% | 75% | Improved | ASHP | Yes | 11677654.0142 | 1680325.7 | 13357979.7142 | 123.1039 | 41.9419 | 21.2374 | 42.99% | 45.33%
15 | 4 | Improved | Current | None | Improved | ASHP | Yes | 12947368.9088 | 2254840.1 | 15202209.0088 | 140.0998 | 68.943 | 24.2326 | 35.12% | 37.62%
15 | 4 | Improved | Current | 75% | Improved | ASHP | Yes | 12030067.9849 | 1627380.6 | 13657448.5849 | 125.8637 | 37.5076 | 21.6968 | 41.71% | 44.15%
15 | 4 | Improved | 25% | None | Improved | ASHP | Yes | 12502498.9457 | 2283524.8 | 14786023.7457 | 136.2644 | 71.1678 | 23.5858 | 36.9% | 39.29%
15 | 4 | Improved | 25% | 75% | Improved | ASHP | Yes | 11601436.0205 | 1651435.9 | 13252871.9205 | 122.1352 | 39.9204 | 21.0674 | 43.44% | 45.77%
15 | 5.5 | Current | Current | None | Improved | ASHP | Yes | 12877216.9146 | 2228323.6 | 15105540.5146 | 139.209 | 67.0149 | 24.0762 | 35.53% | 38.03%
15 | 5.5 | Current | Current | 75% | Improved | ASHP | Yes | 11958815.9908 | 1598959.6 | 13557775.5908 | 124.9451 | 35.5611 | 21.5354 | 42.14% | 44.57%
15 | 5.5 | Current | 25% | None | Improved | ASHP | Yes | 12444378.9505 | 2250708.8 | 14695087.7505 | 135.4263 | 69.3811 | 23.4373 | 37.28% | 39.67%
15 | 5.5 | Current | 25% | 75% | Improved | ASHP | Yes | 11525876.0268 | 1621462 | 13147338.0268 | 121.1627 | 37.8994 | 20.8965 | 43.89% | 46.21%
15 | 5.5 | Improved | Current | None | Improved | ASHP | Yes | 12813877.9198 | 2180593.9 | 14994471.8198 | 138.1854 | 65.2519 | 23.8934 | 36.01% | 38.5%
15 | 5.5 | Improved | Current | 75% | Improved | ASHP | Yes | 11883482.9971 | 1557675.9 | 13441158.8971 | 123.8704 | 33.6243 | 21.3451 | 42.64% | 45.06%
15 | 5.5 | Improved | 25% | None | Improved | ASHP | Yes | 12370956.9566 | 2219445.7 | 14590402.6566 | 134.4616 | 67.4651 | 23.2675 | 37.73% | 40.11%
15 | 5.5 | Improved | 25% | 75% | Improved | ASHP | Yes | 11449227.0331 | 1593128.9 | 13042355.9331 | 120.1952 | 35.8957 | 20.7268 | 44.34% | 46.65%

## Raw
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80
| Run ID | HVAC System | Controls | File Name | Run Date | Gross Floor Area (ft²) | Gross Volume (ft³) | Gross Exterior Walls (ft²) | Gross Exterior Roofs (ft²) | Gross Exterior Floors (ft²) | Gross Windows (ft²) | Gross Skylights (ft²) | Walls (MBTU) | Roofs (MBTU) | Interior Surface (MBTU) | Underground Surface (MBTU) | Infiltration (MBTU) | Window Conduction (MBTU) | Window Solar (MBTU) | Occupants (MBTU) | Lights (MBTU) | Equipment (MBTU) | Source (MBTU) | Total (MBTU) | Total Heating Coil (MBTU) | Under Heated Hours | Under Cooled Hours | $ | $ | Lights (MBTU) | Task Light (MBTU) | Misc. Equip (MBTU) | Space Heating (MBTU) | Space Cooling (MBTU) | Heat Rejection (MBTU) | Pumps & Aux (MBTU) | Ventilation Fans (MBTU) | Refrig Display (MBTU) | Heat Pump Supplimental (MBTU) | Domestic Hot Water (MBTU) | Exterior Usage (MBTU) | Lights (MBTU) | Task Light (MBTU) | Misc. Equip (MBTU) | Space Heating (MBTU) | Space Cooling (MBTU) | Heat Rejection (MBTU) | Pumps & Aux (MBTU) | Ventilation Fans (MBTU) | Refrig Display (MBTU) | Heat Pump Supplimental (MBTU) | Domestic Hot Water (MBTU) | Exterior Usage (MBTU) | Lights (kBTUH) | Task Light (kBTUH) | Misc. Equip (kBTUH) | Space Heating (kBTUH) | Space Cooling (kBTUH) | Heat Rejection (kBTUH) | Pumps & Aux (kBTUH) | Ventilation Fans (kBTUH) | Refrig Display (kBTUH) | Heat Pump Supplimental (kBTUH) | Domestic Hot Water (kBTUH) | Exterior Usage (kBTUH) | Total (kBTUH) | Lights (kBTUH) | Task Light (kBTUH) | Misc. Equip (kBTUH) | Space Heating (kBTUH) | Space Cooling (kBTUH) | Heat Rejection (kBTUH) | Pumps & Aux (kBTUH) | Ventilation Fans (kBTUH) | Refrig Display (kBTUH) | Heat Pump Supplimental (kBTUH) | Domestic Hot Water (kBTUH) | Exterior Usage (kBTUH) | Total (kBTUH)
x | 1 | Current | Current | 1AAAAA | 4/29/2025 9:16:58 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4649.082 | -1111.681 | 0 | -1368.584 | -3177.809 | -10021.72 | 1318.816 | 858.848 | 2408.691 | 3408.915 | 0 | -12333.6 | -37383.625 | 16357 | 0 | 1845054 | 348125 | 7386.8492 | 0 | 10979.3984 | 49.2935 | 4075.2829 | 201.901 | 5412.2521 | 7710.2485 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 35667.7 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0512 | 2450.3309 | 1515.3582 | 876.1296 | 1876.6347 | 0 | 0 | 1651.7814 | 3.0307 | 11938.2686 | 0 | 0 | 0 | 27200 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 28920
| 2 | Current | Current | 1AAAAB | 4/29/2025 9:17:00 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4649.082 | -1111.681 | 0 | -1368.584 | -3177.809 | -10021.72 | 1318.816 | 858.848 | 2408.691 | 3408.915 | 0 | -12333.6 | -24289.506 | 16352 | 0 | 1901395 | 230328 | 7386.8492 | 0 | 10979.3984 | 34.3447 | 4085.73 | 161.5836 | 5579.0814 | 8820.9174 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 25315.6 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0614 | 1367.0306 | 696.4505 | 717.3071 | 2027.0203 | 0 | 0 | 1651.7814 | 3.0307 | 10524.4087 | 0 | 0 | 0 | 22950 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 23320
| 3 | Current | Current | 1AAABA | 4/29/2025 9:17:02 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4807.696 | -1113.906 | 0 | -1368.584 | -3290.236 | -10403.42 | 1390.797 | 950.243 | 2061.176 | 3707.062 | 0 | -12874.56 | -38399.777 | 16451 | 0 | 1763378 | 356735 | 5731.5627 | 0 | 10979.3984 | 50.4949 | 3999.5287 | 191.6553 | 5416.0303 | 7659.6444 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 36647.1 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0478 | 2388.0749 | 1516.5767 | 874.0477 | 1807.6961 | 0 | 0 | 1651.7814 | 3.0307 | 11282.1731 | 0 | 0 | 0 | 27260 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 28980
| 4 | Current | Current | 1AAABB | 4/29/2025 9:17:04 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4807.696 | -1113.906 | 0 | -1368.584 | -3290.236 | -10403.42 | 1390.797 | 950.243 | 2061.176 | 3707.062 | 0 | -12874.56 | -25304.137 | 16446 | 0 | 1819947 | 239172 | 5731.5627 | 0 | 10979.3984 | 35.7509 | 4014.4809 | 150.3208 | 5583.9176 | 8770.4873 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 26321.7 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0307 | 1301.7883 | 627.1501 | 717.1672 | 1957.8053 | 0 | 0 | 1651.7814 | 3.0307 | 9861.5555 | 0 | 0 | 0 | 22980 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 23350
| 5 | Current | Current | 1AABAA | 4/29/2025 9:17:06 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4595.778 | -1108.99 | 0 | -1368.584 | -2647.677 | -9885.926 | 1291.173 | 828.067 | 2336.019 | 3307.493 | 0 | -11844.21 | -36654.961 | 16204 | 0 | 1845239 | 342119 | 7386.8492 | 0 | 10979.3984 | 48.9215 | 4075.1805 | 203.0239 | 5411.1839 | 7714.7093 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 34984.4 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0307 | 2436.0408 | 1515.3582 | 875.1706 | 1881.4606 | 0 | 0 | 1651.7814 | 3.0307 | 11928.4529 | 0 | 0 | 0 | 26620 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 28270
| 6 | Current | Current | 1AABAB | 4/29/2025 9:17:08 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4595.778 | -1108.99 | 0 | -1368.584 | -2647.677 | -9885.926 | 1291.173 | 828.067 | 2336.019 | 3307.493 | 0 | -11844.21 | -23561.143 | 16199 | 0 | 1901592 | 224124 | 7386.8492 | 0 | 10979.3984 | 33.5734 | 4087.0986 | 162.2287 | 5577.45 | 8825.5897 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 24609.8 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0239 | 1352.5357 | 684.1296 | 717.0034 | 2031.8667 | 0 | 0 | 1651.7814 | 3.0307 | 10513.8353 | 0 | 0 | 0 | 22810 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 23180
| 7 | Current | Current | 1AABBA | 4/29/2025 9:17:10 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4757.098 | -1111.448 | 0 | -1368.584 | -2743.786 | -10273.39 | 1361.822 | 918.716 | 2004.662 | 3602.113 | 0 | -12366.99 | -37661.047 | 16288 | 0 | 1763412 | 350527 | 5731.5627 | 0 | 10979.3984 | 49.7986 | 3998.655 | 192.5119 | 5414.6753 | 7662.4362 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 35940.9 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0171 | 2374.9554 | 1498.9282 | 873.1364 | 1812.3923 | 0 | 0 | 1651.7814 | 3.0307 | 11274.0059 | 0 | 0 | 0 | 26990 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 28710
| 8 | Current | Current | 1AABBB | 4/29/2025 9:17:11 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4757.098 | -1111.448 | 0 | -1368.584 | -2743.786 | -10273.39 | 1361.822 | 918.716 | 2004.662 | 3602.113 | 0 | -12366.99 | -24565.689 | 16283 | 0 | 1820010 | 232992 | 5731.5627 | 0 | 10979.3984 | 35.1024 | 4014.7949 | 151.099 | 5581.9688 | 8773.3645 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 25618.6 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0546 | 1288.0852 | 616.2252 | 716.8737 | 1962.5084 | 0 | 0 | 1651.7814 | 3.0307 | 9853.1971 | 0 | 0 | 0 | 22850 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 23210
| 9 | Current | Current | 1ABAAA | 4/29/2025 9:17:13 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4309.447 | -1108.517 | 0 | -1368.584 | -2898.095 | -6715.244 | 1107.69 | 681.33 | 1973.182 | 2791.834 | 0 | -9845.851 | -34408.852 | 16095 | 0 | 1847149 | 323638 | 7386.8492 | 0 | 10979.3984 | 47.6587 | 4094.9621 | 208.3106 | 5407.317 | 7736.5796 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 32881.8 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 17.9795 | 2453.522 | 1515.3582 | 876.232 | 1902.6142 | 0 | 0 | 1651.7814 | 3.0307 | 12003.1389 | 0 | 0 | 0 | 25800 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27520
| 10 | Current | Current | 1ABAAB | 4/29/2025 9:17:15 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4309.447 | -1108.517 | 0 | -1368.584 | -2898.095 | -6715.244 | 1107.69 | 681.33 | 1973.182 | 2791.834 | 0 | -9845.851 | -21317.035 | 16093 | 0 | 1903385 | 204957 | 7386.8492 | 0 | 10979.3984 | 31.6348 | 4107.2488 | 167.4573 | 5571.5388 | 8847.2552 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 22429.2 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0205 | 1371.5323 | 701.8737 | 716.4675 | 2053.1773 | 0 | 0 | 1651.7814 | 3.0307 | 10592.5247 | 0 | 0 | 0 | 22340 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22700
| 11 | Current | Current | 1ABABA | 4/29/2025 9:17:17 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4495.643 | -1111.085 | 0 | -1368.584 | -3031.79 | -7048.75 | 1175.832 | 774.124 | 1735.96 | 3092.879 | 0 | -10277.06 | -35374.078 | 16167 | 0 | 1764904 | 331618 | 5731.5627 | 0 | 10979.3984 | 48.3481 | 4014.5492 | 196.6348 | 5410.4978 | 7680.6922 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 33789.7 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0341 | 2391.1397 | 1521.0988 | 874.1399 | 1832.7405 | 0 | 0 | 1651.7814 | 3.0307 | 11343.197 | 0 | 0 | 0 | 25860 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27580
| 12 | Current | Current | 1ABABB | 4/29/2025 9:17:19 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4495.643 | -1111.085 | 0 | -1368.584 | -3031.79 | -7048.75 | 1175.832 | 774.124 | 1735.96 | 3092.879 | 0 | -10277.06 | -22280.221 | 16166 | 0 | 1821491 | 213477 | 5731.5627 | 0 | 10979.3984 | 32.9317 | 4032.2556 | 155.8328 | 5576.0268 | 8791.6887 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 23398.5 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0512 | 1305.0682 | 632.1331 | 716.3173 | 1982.9384 | 0 | 0 | 1651.7814 | 3.0307 | 9924.8729 | 0 | 0 | 0 | 22390 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22750
| 13 | Current | Current | 1ABBAA | 4/29/2025 9:17:21 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4243.205 | -1104.798 | 0 | -1368.584 | -2400.513 | -6592.154 | 1079.972 | 649.019 | 1896.283 | 2684.943 | 0 | -9399.036 | -33679.047 | 15965 | 0 | 1847648 | 317638 | 7386.8492 | 0 | 10979.3984 | 47.4096 | 4097.7232 | 209.9181 | 5406.0371 | 7744.6683 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 32199.2 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0478 | 2439.2421 | 1515.3582 | 875.4334 | 1907.5357 | 0 | 0 | 1651.7814 | 3.0307 | 11993.2447 | 0 | 0 | 0 | 25530 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27250
| 14 | Current | Current | 1ABBAB | 4/29/2025 9:17:23 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4243.205 | -1104.798 | 0 | -1368.584 | -2400.513 | -6592.154 | 1079.972 | 649.019 | 1896.283 | 2684.943 | 0 | -9399.036 | -20588.287 | 15960 | 0 | 1903894 | 198663 | 7386.8492 | 0 | 10979.3984 | 30.744 | 4111.4433 | 169.174 | 5569.6002 | 8855.3201 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 21713.2 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 17.9863 | 1358.4231 | 689.5836 | 716.0921 | 2058.1432 | 0 | 0 | 1651.7814 | 3.0307 | 10581.8285 | 0 | 0 | 0 | 22110 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22480
| 15 | Current | Current | 1ABBBA | 4/29/2025 9:17:25 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4422.426 | -1108.017 | 0 | -1368.584 | -2509.886 | -6912.568 | 1144.307 | 734.823 | 1667.032 | 2965.544 | 0 | -9809.775 | -34631.703 | 16019 | 0 | 1765271 | 325516 | 5731.5627 | 0 | 10979.3984 | 47.9761 | 4016.5321 | 197.5461 | 5409.2282 | 7687.4738 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 33095.6 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0341 | 2378.0442 | 1502.7166 | 873.3242 | 1837.5016 | 0 | 0 | 1651.7814 | 3.0307 | 11334.8967 | 0 | 0 | 0 | 25600 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27320
| 16 | Current | Current | 1ABBBB | 4/29/2025 9:17:27 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4422.426 | -1108.017 | 0 | -1368.584 | -2509.886 | -6912.568 | 1144.307 | 734.823 | 1667.032 | 2965.544 | 0 | -9809.775 | -21538.545 | 16018 | 0 | 1821883 | 207223 | 5731.5627 | 0 | 10979.3984 | 32.3549 | 4035.399 | 157.0341 | 5574.2146 | 8798.3064 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 22687.1 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 17.9932 | 1291.3378 | 621.1433 | 715.9522 | 1987.72 | 0 | 0 | 1651.7814 | 3.0307 | 9916.1835 | 0 | 0 | 0 | 22170 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22540
| 17 | Current | Current | 1ACAAA | 4/29/2025 9:17:29 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4114.481 | -1106.279 | 0 | -1368.584 | -2740.485 | -5198.971 | 1001.451 | 596.498 | 1758.965 | 2485.545 | 0 | -8686.34 | -32932.848 | 15967 | 0 | 1848689 | 311515 | 7386.8492 | 0 | 10979.3984 | 47.099 | 4108.9416 | 212.8942 | 5404.7231 | 7754.9004 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 31502.7 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0375 | 2455.2216 | 1515.3582 | 876.3617 | 1916.0101 | 0 | 0 | 1651.7814 | 3.0307 | 12036.429 | 0 | 0 | 0 | 25270 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26990
| 18 | Current | Current | 1ACAAB | 4/29/2025 9:17:31 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4114.481 | -1106.279 | 0 | -1368.584 | -2740.485 | -5198.971 | 1001.451 | 596.498 | 1758.965 | 2485.545 | 0 | -8686.34 | -19842.918 | 15964 | 0 | 1904861 | 192201 | 7386.8492 | 0 | 10979.3984 | 29.959 | 4122.3444 | 171.8771 | 5567.5832 | 8865.675 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 20978 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0307 | 1374.6074 | 704.6552 | 715.4982 | 2066.6824 | 0 | 0 | 1651.7814 | 3.0307 | 10627.5759 | 0 | 0 | 0 | 21890 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22260
| 19 | Current | Current | 1ACABA | 4/29/2025 9:17:33 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4295.404 | -1109.318 | 0 | -1368.584 | -2870.131 | -5462.616 | 1060.205 | 676.467 | 1555.727 | 2751.975 | 0 | -9061.679 | -33866.781 | 16048 | 0 | 1766131 | 319288 | 5731.5627 | 0 | 10979.3984 | 47.7372 | 4026.2181 | 199.9181 | 5407.6412 | 7696.0744 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 32387 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0546 | 2392.8155 | 1523.0681 | 874.2047 | 1845.6517 | 0 | 0 | 1651.7814 | 3.0307 | 11374.6612 | 0 | 0 | 0 | 25340 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27060
| 20 | Current | Current | 1ACABB | 4/29/2025 9:17:35 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4295.404 | -1109.318 | 0 | -1368.584 | -2870.131 | -5462.616 | 1060.205 | 676.467 | 1555.727 | 2751.975 | 0 | -9061.679 | -20774.471 | 16047 | 0 | 1822687 | 200691 | 5731.5627 | 0 | 10979.3984 | 31.6212 | 4044.8836 | 159.3072 | 5572.0917 | 8806.9924 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 21943.9 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0375 | 1306.8429 | 634.7303 | 715.4641 | 1995.9043 | 0 | 0 | 1651.7814 | 3.0307 | 9957.6306 | 0 | 0 | 0 | 21960 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22330
| 21 | Current | Current | 1ACBAA | 4/29/2025 9:17:37 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4051.932 | -1102.444 | 0 | -1368.584 | -2267.498 | -5103.075 | 974.032 | 569.918 | 1694.583 | 2392.346 | 0 | -8262.652 | -32205.266 | 15822 | 0 | 1849418 | 305435 | 7386.8492 | 0 | 10979.3984 | 46.7782 | 4113.8017 | 214.5904 | 5403.8357 | 7765.4908 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 30811 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0819 | 2440.9213 | 1515.3582 | 875.5699 | 1920.9998 | 0 | 0 | 1651.7814 | 3.0307 | 12026.412 | 0 | 0 | 0 | 24970 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26690
| 22 | Current | Current | 1ACBAB | 4/29/2025 9:17:39 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4051.932 | -1102.444 | 0 | -1368.584 | -2267.498 | -5103.075 | 974.032 | 569.918 | 1694.583 | 2392.346 | 0 | -8262.652 | -19116.518 | 15820 | 0 | 1905603 | 185889 | 7386.8492 | 0 | 10979.3984 | 29.1502 | 4128.3375 | 173.6416 | 5566.1668 | 8876.3952 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 20259.9 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0512 | 1361.4709 | 692.3208 | 714.7815 | 2071.7234 | 0 | 0 | 1651.7814 | 3.0307 | 10616.5896 | 0 | 0 | 0 | 21580 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21950
| 23 | Current | Current | 1ACBBA | 4/29/2025 9:17:41 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4223.139 | -1105.568 | 0 | -1368.584 | -2371.898 | -5352.303 | 1031.065 | 641.732 | 1493.74 | 2636.707 | 0 | -8618.247 | -33124.742 | 15911 | 0 | 1766672 | 313209 | 5731.5627 | 0 | 10979.3984 | 47.4232 | 4029.2317 | 201.4539 | 5406.5798 | 7704.7161 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 31695.4 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0819 | 2379.7609 | 1505.0477 | 873.4641 | 1850.5084 | 0 | 0 | 1651.7814 | 3.0307 | 11366.3506 | 0 | 0 | 0 | 25050 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26770
| 24 | Current | Current | 1ACBBB | 4/29/2025 9:17:43 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4223.139 | -1105.568 | 0 | -1368.584 | -2371.898 | -5352.303 | 1031.065 | 641.732 | 1493.74 | 2636.707 | 0 | -8618.247 | -20033.332 | 15908 | 0 | 1823245 | 194264 | 5731.5627 | 0 | 10979.3984 | 30.7338 | 4049.5048 | 160.744 | 5570.392 | 8815.7262 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 21212.7 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0512 | 1293.1364 | 623.7952 | 714.8054 | 2000.7814 | 0 | 0 | 1651.7814 | 3.0307 | 9948.9377 | 0 | 0 | 0 | 21670 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22030
| 25 | Current | Current | 1BAAAA | 4/29/2025 9:17:45 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2686.747 | -1110.092 | 0 | -1368.584 | -2999.972 | -9452.697 | 1203.151 | 729.658 | 2102.148 | 2990.746 | 0 | -10592.39 | -35295.012 | 16167 | 0 | 1845151 | 330974 | 7386.8492 | 0 | 10979.3984 | 48.2423 | 4079.4195 | 204.5051 | 5408.1804 | 7710.7912 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 33716.4 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.041 | 2451.3718 | 1515.3582 | 876.0204 | 1872.1807 | 0 | 0 | 1651.7814 | 3.0307 | 11942.2618 | 0 | 0 | 0 | 26030 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27760
| 26 | Current | Current | 1BAAAB | 4/29/2025 9:17:47 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2686.747 | -1110.092 | 0 | -1368.584 | -2999.972 | -9452.697 | 1203.151 | 729.658 | 2102.148 | 2990.746 | 0 | -10592.39 | -22201.684 | 16165 | 0 | 1901373 | 212554 | 7386.8492 | 0 | 10979.3984 | 32.5836 | 4090.5799 | 163 | 5573.3511 | 8821.6204 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 23293.5 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0239 | 1368.6279 | 699.1057 | 716.5426 | 2022.5391 | 0 | 0 | 1651.7814 | 3.0307 | 10528.4053 | 0 | 0 | 0 | 22520 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22890
| 27 | Current | Current | 1BAABA | 4/29/2025 9:17:49 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2787.15 | -1112.567 | 0 | -1368.584 | -3133.969 | -9907.344 | 1276.18 | 828.088 | 1841.14 | 3306.102 | 0 | -11058.11 | -36287.699 | 16250 | 0 | 1763221 | 339162 | 5731.5627 | 0 | 10979.3984 | 49.0785 | 4002.0952 | 192.6519 | 5411.6787 | 7658.4226 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 34647.9 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0546 | 2388.6756 | 1517.5459 | 873.9078 | 1802.9111 | 0 | 0 | 1651.7814 | 3.0307 | 11284.2619 | 0 | 0 | 0 | 26090 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27820
| 28 | Current | Current | 1BAABB | 4/29/2025 9:17:51 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2787.15 | -1112.567 | 0 | -1368.584 | -3133.969 | -9907.344 | 1276.18 | 828.088 | 1841.14 | 3306.102 | 0 | -11058.11 | -23192.789 | 16247 | 0 | 1819766 | 221323 | 5731.5627 | 0 | 10979.3984 | 33.9863 | 4017.9007 | 151.7099 | 5578.0814 | 8769.3099 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 24291.1 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0512 | 1302.5084 | 629.2559 | 716.4027 | 1953.0067 | 0 | 0 | 1651.7814 | 3.0307 | 9863.5726 | 0 | 0 | 0 | 22570 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22940
| 29 | Current | Current | 1BABAA | 4/29/2025 9:17:53 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2650.875 | -1106.92 | 0 | -1368.584 | -2489.491 | -9285.394 | 1174.579 | 695.408 | 2021.372 | 2878.022 | 0 | -10131.88 | -34561.188 | 16031 | 0 | 1845358 | 324934 | 7386.8492 | 0 | 10979.3984 | 47.843 | 4079.986 | 205.4198 | 5406.8221 | 7715.5898 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 33029.3 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18 | 2437.0373 | 1515.3582 | 875.0614 | 1876.976 | 0 | 0 | 1651.7814 | 3.0307 | 11932.3574 | 0 | 0 | 0 | 25770 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27490
| 30 | Current | Current | 1BABAB | 4/29/2025 9:17:55 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2650.875 | -1106.92 | 0 | -1368.584 | -2489.491 | -9285.394 | 1174.579 | 695.408 | 2021.372 | 2878.022 | 0 | -10131.88 | -21468.625 | 16029 | 0 | 1901633 | 206329 | 7386.8492 | 0 | 10979.3984 | 32.0068 | 4092.3922 | 164.6007 | 5571.4296 | 8826.3918 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 22585.3 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.041 | 1355.4538 | 686.7986 | 716.3412 | 2027.3548 | 0 | 0 | 1651.7814 | 3.0307 | 10517.8387 | 0 | 0 | 0 | 22330 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22690
| 31 | Current | Current | 1BABBA | 4/29/2025 9:17:57 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2750.431 | -1109.786 | 0 | -1368.584 | -2601.236 | -9733.007 | 1244.313 | 789.069 | 1772.734 | 3180.707 | 0 | -10576.22 | -35542.328 | 16105 | 0 | 1763351 | 333061 | 5731.5627 | 0 | 10979.3984 | 48.5939 | 4001.7812 | 193.6826 | 5410.4364 | 7662.2451 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 33953.9 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0375 | 2375.5356 | 1499.5425 | 872.9897 | 1807.5528 | 0 | 0 | 1651.7814 | 3.0307 | 11276.1185 | 0 | 0 | 0 | 25830 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27550
| 32 | Current | Current | 1BABBB | 4/29/2025 9:17:59 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2750.431 | -1109.786 | 0 | -1368.584 | -2601.236 | -9733.007 | 1244.313 | 789.069 | 1772.734 | 3180.707 | 0 | -10576.22 | -22447.779 | 16103 | 0 | 1819921 | 214976 | 5731.5627 | 0 | 10979.3984 | 33.3413 | 4019.1089 | 152.6485 | 5576.1804 | 8773.1085 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 23569.1 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0478 | 1288.7507 | 618.2013 | 716.2013 | 1957.6551 | 0 | 0 | 1651.7814 | 3.0307 | 9855.2381 | 0 | 0 | 0 | 22380 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22740
| 33 | Current | Current | 1BBAAA | 4/29/2025 9:18:01 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2487.478 | -1105.918 | 0 | -1368.584 | -2699.953 | -6244.541 | 988.083 | 567.608 | 1692.615 | 2400.977 | 0 | -8257.193 | -32329.039 | 15916 | 0 | 1847646 | 306575 | 7386.8492 | 0 | 10979.3984 | 46.9863 | 4102.928 | 211.9727 | 5403.0064 | 7740.8048 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 30940.8 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0478 | 2454.5083 | 1515.3582 | 876.1364 | 1898.191 | 0 | 0 | 1651.7814 | 3.0307 | 12007.7055 | 0 | 0 | 0 | 24990 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26710
| 34 | Current | Current | 1BBAAB | 4/29/2025 9:18:03 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2487.478 | -1105.918 | 0 | -1368.584 | -2699.953 | -6244.541 | 988.083 | 567.608 | 1692.615 | 2400.977 | 0 | -8257.193 | -19239.438 | 15913 | 0 | 1903784 | 187012 | 7386.8492 | 0 | 10979.3984 | 29.5222 | 4116.5116 | 170.5631 | 5565.7436 | 8851.5214 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 20387.6 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 17.9966 | 1374.505 | 704.5085 | 715.3515 | 2048.7234 | 0 | 0 | 1651.7814 | 3.0307 | 10597.2346 | 0 | 0 | 0 | 21640 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22000
| 35 | Current | Current | 1BBABA | 4/29/2025 9:18:05 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2576.924 | -1109.172 | 0 | -1368.584 | -2817.203 | -6532.413 | 1045.754 | 633.641 | 1483.308 | 2629.841 | 0 | -8611.753 | -33259.871 | 15994 | 0 | 1765155 | 314413 | 5731.5627 | 0 | 10979.3984 | 47.6962 | 4020.8188 | 198.7781 | 5405.9415 | 7682.9721 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 31832.4 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0751 | 2391.6585 | 1521.7746 | 874.0033 | 1827.9248 | 0 | 0 | 1651.7814 | 3.0307 | 11345.9479 | 0 | 0 | 0 | 25070 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26790
| 36 | Current | Current | 1BBABB | 4/29/2025 9:18:06 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2576.924 | -1109.172 | 0 | -1368.584 | -2817.203 | -6532.413 | 1045.754 | 633.641 | 1483.308 | 2629.841 | 0 | -8611.753 | -20167.469 | 15991 | 0 | 1821665 | 195432 | 5731.5627 | 0 | 10979.3984 | 31.1195 | 4039.416 | 158.0034 | 5570.0337 | 8793.9788 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 21345.6 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0239 | 1305.6722 | 634.1228 | 714.8429 | 1978.092 | 0 | 0 | 1651.7814 | 3.0307 | 9927.5555 | 0 | 0 | 0 | 21710 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22080
| 37 | Current | Current | 1BBBAA | 4/29/2025 9:18:08 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2453.632 | -1102.213 | 0 | -1368.584 | -2235.824 | -6131.729 | 961.294 | 543.122 | 1633.018 | 2314.471 | 0 | -7840.077 | -31598.727 | 15768 | 0 | 1848197 | 300448 | 7386.8492 | 0 | 10979.3984 | 46.6382 | 4106.5321 | 213.0068 | 5402.0337 | 7749.542 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 30243.7 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0375 | 2440.2114 | 1515.3582 | 875.3446 | 1903.0886 | 0 | 0 | 1651.7814 | 3.0307 | 11997.8249 | 0 | 0 | 0 | 24670 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26390
| 38 | Current | Current | 1BBBAB | 4/29/2025 9:18:10 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2453.632 | -1102.213 | 0 | -1368.584 | -2235.824 | -6131.729 | 961.294 | 543.122 | 1633.018 | 2314.471 | 0 | -7840.077 | -18510.389 | 15766 | 0 | 1904405 | 180585 | 7386.8492 | 0 | 10979.3984 | 28.6246 | 4121.6208 | 172.4641 | 5564.4364 | 8860.3064 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 19656.5 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0273 | 1361.3446 | 695.6348 | 714.1604 | 2053.6585 | 0 | 0 | 1651.7814 | 3.0307 | 10586.494 | 0 | 0 | 0 | 21280 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21640
| 39 | Current | Current | 1BBBBA | 4/29/2025 9:18:12 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2537.231 | -1105.255 | 0 | -1368.584 | -2328.202 | -6398.494 | 1015.841 | 601.014 | 1424.397 | 2518.798 | 0 | -8177.714 | -32512.617 | 15846 | 0 | 1765722 | 308219 | 5731.5627 | 0 | 10979.3984 | 47.3925 | 4024.4126 | 200.1706 | 5404.8289 | 7691.8082 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 31127.7 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0341 | 2378.5391 | 1503.7951 | 873.2149 | 1832.6551 | 0 | 0 | 1651.7814 | 3.0307 | 11337.6475 | 0 | 0 | 0 | 24760 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26480
| 40 | Current | Current | 1BBBBB | 4/29/2025 9:18:14 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2537.231 | -1105.255 | 0 | -1368.584 | -2328.202 | -6398.494 | 1015.841 | 601.014 | 1424.397 | 2518.798 | 0 | -8177.714 | -19421.285 | 15845 | 0 | 1822226 | 188976 | 5731.5627 | 0 | 10979.3984 | 30.2253 | 4044.2932 | 159.4403 | 5568.3204 | 8802.5317 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 20611.2 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0478 | 1291.9112 | 623.1399 | 714.0955 | 1982.836 | 0 | 0 | 1651.7814 | 3.0307 | 9918.8183 | 0 | 0 | 0 | 21370 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21740
| 41 | Current | Current | 1BCAAA | 4/29/2025 9:18:16 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2379.674 | -1103.608 | 0 | -1368.584 | -2542.453 | -4809.708 | 875.353 | 499.181 | 1514.865 | 2137.203 | 0 | -7177.425 | -30867.963 | 15784 | 0 | 1849343 | 294493 | 7386.8492 | 0 | 10979.3984 | 46.4846 | 4119.1123 | 216.4266 | 5401.0781 | 7759.7331 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 29566.2 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0341 | 2456.2216 | 1515.3582 | 876.2764 | 1911.6312 | 0 | 0 | 1651.7814 | 3.0307 | 12041.4563 | 0 | 0 | 0 | 24340 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26060
| 42 | Current | Current | 1BCAAB | 4/29/2025 9:18:18 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2379.674 | -1103.608 | 0 | -1368.584 | -2542.453 | -4809.708 | 875.353 | 499.181 | 1514.865 | 2137.203 | 0 | -7177.425 | -17781.289 | 15781 | 0 | 1905412 | 174154 | 7386.8492 | 0 | 10979.3984 | 27.7099 | 4133.143 | 175.4027 | 5562.8118 | 8870.4122 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 18924.9 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0478 | 1377.6313 | 725.0409 | 715.3856 | 2062.2695 | 0 | 0 | 1651.7814 | 3.0307 | 10632.8012 | 0 | 0 | 0 | 20920 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21290
| 43 | Current | Current | 1BCABA | 4/29/2025 9:18:20 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2466.026 | -1106.774 | 0 | -1368.584 | -2650.19 | -5027.251 | 925.345 | 554.594 | 1328.401 | 2325.755 | 0 | -7484.73 | -31757.906 | 15856 | 0 | 1766714 | 301968 | 5731.5627 | 0 | 10979.3984 | 47.0648 | 4035.1908 | 203.4573 | 5403.4091 | 7701.1905 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 30416.6 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0887 | 2393.3513 | 1523.9077 | 874.0989 | 1840.9043 | 0 | 0 | 1651.7814 | 3.0307 | 11377.7294 | 0 | 0 | 0 | 24430 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26160
| 44 | Current | Current | 1BCABB | 4/29/2025 9:18:22 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2466.026 | -1106.774 | 0 | -1368.584 | -2650.19 | -5027.251 | 925.345 | 554.594 | 1328.401 | 2325.755 | 0 | -7484.73 | -18667.867 | 15854 | 0 | 1823108 | 182290 | 5731.5627 | 0 | 10979.3984 | 29.3345 | 4054.887 | 161.529 | 5566.4671 | 8811.9037 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 19850.4 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0375 | 1307.4675 | 636.8122 | 713.604 | 1991.1295 | 0 | 0 | 1651.7814 | 3.0307 | 9960.6784 | 0 | 0 | 0 | 21030 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21400
| 45 | Current | Current | 1BCBAA | 4/29/2025 9:18:24 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2340.72 | -1099.367 | 0 | -1368.584 | -2093.955 | -4702.761 | 846.968 | 474.036 | 1453.507 | 2047.615 | 0 | -6783.262 | -30145.795 | 15633 | 0 | 1850063 | 288599 | 7386.8492 | 0 | 10979.3984 | 46.3072 | 4123.3785 | 218.488 | 5400.3647 | 7770.0505 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 28895.6 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0341 | 2441.952 | 1515.3582 | 875.488 | 1916.662 | 0 | 0 | 1651.7814 | 3.0307 | 12031.5348 | 0 | 0 | 0 | 23960 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 25680
| 46 | Current | Current | 1BCBAB | 4/29/2025 9:18:27 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2340.72 | -1099.367 | 0 | -1368.584 | -2093.955 | -4702.761 | 846.968 | 474.036 | 1453.507 | 2047.615 | 0 | -6783.262 | -17060.82 | 15632 | 0 | 1906145 | 167817 | 7386.8492 | 0 | 10979.3984 | 26.7986 | 4139.0645 | 177.331 | 5561.3716 | 8880.9617 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 18203.9 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 17.9932 | 1364.4845 | 722.5528 | 714.1979 | 2067.3582 | 0 | 0 | 1651.7814 | 3.0307 | 10621.9309 | 0 | 0 | 0 | 20480 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 20850
| 47 | Current | Current | 1BCBBA | 4/29/2025 9:18:29 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2426.571 | -1102.708 | 0 | -1368.584 | -2185.182 | -4918.819 | 895.932 | 526.389 | 1277.256 | 2228.199 | 0 | -7074.087 | -31013.621 | 15692 | 0 | 1767354 | 295831 | 5731.5627 | 0 | 10979.3984 | 46.7508 | 4039.1328 | 205.0341 | 5402.4842 | 7710.9038 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 29718.4 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0205 | 2380.307 | 1505.9146 | 873.3583 | 1845.819 | 0 | 0 | 1651.7814 | 3.0307 | 11369.5622 | 0 | 0 | 0 | 24060 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 25780
| 48 | Current | Current | 1BCBBB | 4/29/2025 9:18:31 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2426.571 | -1102.708 | 0 | -1368.584 | -2185.182 | -4918.819 | 895.932 | 526.389 | 1277.256 | 2228.199 | 0 | -7074.087 | -17924.758 | 15690 | 0 | 1823765 | 175719 | 5731.5627 | 0 | 10979.3984 | 28.3515 | 4060.3683 | 163 | 5564.9756 | 8821.7877 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 19102.9 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 17.9829 | 1293.7644 | 634.901 | 712.4709 | 1996.0647 | 0 | 0 | 1651.7814 | 3.0307 | 9952.0913 | 0 | 0 | 0 | 20600 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 20970
| 49 | Current | Current | 1CAAAA | 4/29/2025 9:18:33 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2061.734 | -1109.454 | 0 | -1368.584 | -2933.382 | -9236.546 | 1162.833 | 685.568 | 1996.693 | 2846.548 | 0 | -10018.06 | -34575.945 | 16118 | 0 | 1845109 | 325094 | 7386.8492 | 0 | 10979.3984 | 47.9556 | 4080.2693 | 205.256 | 5406.5661 | 7710.1564 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 33047.6 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0307 | 2451.6517 | 1515.3582 | 875.9794 | 1870.6551 | 0 | 0 | 1651.7814 | 3.0307 | 11943.04 | 0 | 0 | 0 | 25780 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27510
| 50 | Current | Current | 1CAAAB | 4/29/2025 9:18:35 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2061.734 | -1109.454 | 0 | -1368.584 | -2933.382 | -9236.546 | 1162.833 | 685.568 | 1996.693 | 2846.548 | 0 | -10018.06 | -21483.166 | 16114 | 0 | 1901290 | 206428 | 7386.8492 | 0 | 10979.3984 | 32.1092 | 4091.5457 | 163.6348 | 5571.1907 | 8820.8457 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 22596.6 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0341 | 1369.4333 | 699.8498 | 716.4743 | 2021.0067 | 0 | 0 | 1651.7814 | 3.0307 | 10529.1834 | 0 | 0 | 0 | 22340 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22710
| 51 | Current | Current | 1CAABA | 4/29/2025 9:18:37 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2132.7 | -1112.068 | 0 | -1368.584 | -3066.541 | -9686.394 | 1232.179 | 778.36 | 1753.213 | 3146.58 | 0 | -10455.95 | -35559.191 | 16182 | 0 | 1763195 | 333257 | 5731.5627 | 0 | 10979.3984 | 48.7543 | 4003.0133 | 193.3891 | 5410.2248 | 7657.9686 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 33976.2 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0375 | 2388.7711 | 1517.7029 | 873.8566 | 1801.2592 | 0 | 0 | 1651.7814 | 3.0307 | 11284.4359 | 0 | 0 | 0 | 25850 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27570
| 52 | Current | Current | 1CAABB | 4/29/2025 9:18:39 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2132.7 | -1112.068 | 0 | -1368.584 | -3066.541 | -9686.394 | 1232.179 | 778.36 | 1753.213 | 3146.58 | 0 | -10455.95 | -22464.572 | 16180 | 0 | 1819699 | 215170 | 5731.5627 | 0 | 10979.3984 | 33.4505 | 4019.0236 | 152.3345 | 5576.0064 | 8768.6819 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 23591.1 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0546 | 1302.6381 | 629.7406 | 716.2252 | 1951.3411 | 0 | 0 | 1651.7814 | 3.0307 | 9863.6749 | 0 | 0 | 0 | 22390 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22760
| 53 | Current | Current | 1CABAA | 4/29/2025 9:18:41 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2035.671 | -1105.962 | 0 | -1368.584 | -2432.857 | -9069.122 | 1132.89 | 652.866 | 1919.648 | 2738.887 | 0 | -9567.904 | -33840.516 | 15977 | 0 | 1845441 | 319114 | 7386.8492 | 0 | 10979.3984 | 47.7031 | 4081.9621 | 206.1092 | 5405.3716 | 7716.327 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 32367.2 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.041 | 2437.3104 | 1515.3582 | 875.0238 | 1875.4435 | 0 | 0 | 1651.7814 | 3.0307 | 11933.197 | 0 | 0 | 0 | 25520 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27240
| 54 | Current | Current | 1CABAB | 4/29/2025 9:18:43 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2035.671 | -1105.962 | 0 | -1368.584 | -2432.857 | -9069.122 | 1132.89 | 652.866 | 1919.648 | 2738.887 | 0 | -9567.904 | -20748.57 | 15974 | 0 | 1901665 | 200078 | 7386.8492 | 0 | 10979.3984 | 31.1775 | 4094.5457 | 165.3618 | 5569.5285 | 8826.9003 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 21874.2 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0512 | 1356.2456 | 687.4812 | 716.0819 | 2025.8121 | 0 | 0 | 1651.7814 | 3.0307 | 10518.6305 | 0 | 0 | 0 | 22110 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22480
| 55 | Current | Current | 1CABBA | 4/29/2025 9:18:45 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2106.267 | -1109.082 | 0 | -1368.584 | -2542.893 | -9507.826 | 1201.892 | 739.842 | 1685.911 | 3022.081 | 0 | -9984.928 | -34811.031 | 16042 | 0 | 1763399 | 327171 | 5731.5627 | 0 | 10979.3984 | 48.3618 | 4003.5628 | 194.5051 | 5408.8357 | 7662.5591 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 33283.9 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0546 | 2375.621 | 1499.6893 | 872.9385 | 1805.8906 | 0 | 0 | 1651.7814 | 3.0307 | 11276.2789 | 0 | 0 | 0 | 25580 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27300
| 56 | Current | Current | 1CABBB | 4/29/2025 9:18:46 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2106.267 | -1109.082 | 0 | -1368.584 | -2542.893 | -9507.826 | 1201.892 | 739.842 | 1685.911 | 3022.081 | 0 | -9984.928 | -21716.938 | 16040 | 0 | 1819923 | 208802 | 5731.5627 | 0 | 10979.3984 | 32.7713 | 4020.8768 | 153.1672 | 5574.2589 | 8773.3303 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 22866.7 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0171 | 1288.8531 | 618.7542 | 715.959 | 1955.9828 | 0 | 0 | 1651.7814 | 3.0307 | 9855.3814 | 0 | 0 | 0 | 22170 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22540
| 57 | Current | Current | 1CBAAA | 4/29/2025 9:18:48 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1919.807 | -1105.069 | 0 | -1368.584 | -2635.786 | -6090.363 | 944.852 | 536.355 | 1614.435 | 2288.108 | 0 | -7735.858 | -31616.396 | 15854 | 0 | 1847741 | 300614 | 7386.8492 | 0 | 10979.3984 | 46.7235 | 4105.3478 | 212.6792 | 5401.689 | 7741.3645 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 30262.5 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0137 | 2454.7643 | 1515.3582 | 876.1023 | 1896.6756 | 0 | 0 | 1651.7814 | 3.0307 | 12008.6884 | 0 | 0 | 0 | 24680 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26400
| 58 | Current | Current | 1CBAAB | 4/29/2025 9:18:50 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1919.807 | -1105.069 | 0 | -1368.584 | -2635.786 | -6090.363 | 944.852 | 536.355 | 1614.435 | 2288.108 | 0 | -7735.858 | -18527.842 | 15851 | 0 | 1903887 | 180729 | 7386.8492 | 0 | 10979.3984 | 28.7031 | 4119.4058 | 171.7133 | 5564.2248 | 8852.0914 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 19672.9 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0546 | 1375.2934 | 709.6348 | 715.3173 | 2047.1944 | 0 | 0 | 1651.7814 | 3.0307 | 10598.2176 | 0 | 0 | 0 | 21300 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21670
| 59 | Current | Current | 1CBABA | 4/29/2025 9:18:52 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1980.672 | -1108.276 | 0 | -1368.584 | -2743.472 | -6354.567 | 999.919 | 592.936 | 1407.051 | 2487.569 | 0 | -8068.097 | -32531.975 | 15928 | 0 | 1765318 | 308418 | 5731.5627 | 0 | 10979.3984 | 47.4812 | 4023.5321 | 200.0751 | 5404.3682 | 7684.3134 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 31150.4 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0512 | 2391.7268 | 1521.5971 | 873.9556 | 1826.2797 | 0 | 0 | 1651.7814 | 3.0307 | 11346.2926 | 0 | 0 | 0 | 24760 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26490
| 60 | Current | Current | 1CBABB | 4/29/2025 9:18:54 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1980.672 | -1108.276 | 0 | -1368.584 | -2743.472 | -6354.567 | 999.919 | 592.936 | 1407.051 | 2487.569 | 0 | -8068.097 | -19440.264 | 15925 | 0 | 1821769 | 189123 | 5731.5627 | 0 | 10979.3984 | 30.3311 | 4042.5218 | 158.5665 | 5568.1088 | 8795.2894 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 20627.9 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0444 | 1305.7883 | 634.6416 | 714.0716 | 1976.4401 | 0 | 0 | 1651.7814 | 3.0307 | 9927.9139 | 0 | 0 | 0 | 21400 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21770
| 61 | Current | Current | 1CBBAA | 4/29/2025 9:18:56 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1890.967 | -1101.033 | 0 | -1368.584 | -2175.514 | -5960.703 | 915.144 | 509.034 | 1549.085 | 2194.663 | 0 | -7328.874 | -30886.877 | 15705 | 0 | 1848407 | 294632 | 7386.8492 | 0 | 10979.3984 | 46.4881 | 4109.8666 | 214.4368 | 5400.9757 | 7750.583 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 29582 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0546 | 2440.4742 | 1515.3582 | 875.3139 | 1901.5903 | 0 | 0 | 1651.7814 | 3.0307 | 11998.8557 | 0 | 0 | 0 | 24330 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26050
| 62 | Current | Current | 1CBBAB | 4/29/2025 9:18:57 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1890.967 | -1101.033 | 0 | -1368.584 | -2175.514 | -5960.703 | 915.144 | 509.034 | 1549.085 | 2194.663 | 0 | -7328.874 | -17799.848 | 15704 | 0 | 1904524 | 174327 | 7386.8492 | 0 | 10979.3984 | 27.7645 | 4124.7505 | 173.4812 | 5562.8118 | 8861.2723 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 18944.6 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0444 | 1362.1364 | 707.3208 | 714.1262 | 2052.1568 | 0 | 0 | 1651.7814 | 3.0307 | 10587.5418 | 0 | 0 | 0 | 20900 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21270
| 63 | Current | Current | 1CBBBA | 4/29/2025 9:18:59 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1953.508 | -1104.263 | 0 | -1368.584 | -2267.42 | -6226.989 | 968.362 | 564.539 | 1355.358 | 2387.511 | 0 | -7644.995 | -31783.957 | 15779 | 0 | 1765869 | 302184 | 5731.5627 | 0 | 10979.3984 | 47.0819 | 4026.7949 | 201.5188 | 5403.2794 | 7693.1734 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 30441.2 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0853 | 2378.6176 | 1503.7814 | 873.1774 | 1831.0237 | 0 | 0 | 1651.7814 | 3.0307 | 11338.0571 | 0 | 0 | 0 | 24420 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26140
| 64 | Current | Current | 1CBBBB | 4/29/2025 9:19:01 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1953.508 | -1104.263 | 0 | -1368.584 | -2267.42 | -6226.989 | 968.362 | 564.539 | 1355.358 | 2387.511 | 0 | -7644.995 | -18693.51 | 15775 | 0 | 1822335 | 182534 | 5731.5627 | 0 | 10979.3984 | 29.3925 | 4047.3341 | 160.0546 | 5566.4842 | 8803.9481 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 19878.2 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0341 | 1292.0238 | 623.6109 | 712.3685 | 1981.2046 | 0 | 0 | 1651.7814 | 3.0307 | 9919.2381 | 0 | 0 | 0 | 21010 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21380
| 65 | Current | Current | 1CCAAA | 4/29/2025 9:19:03 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1837.453 | -1102.529 | 0 | -1368.584 | -2471.037 | -4668.903 | 834.556 | 468.014 | 1436.369 | 2024.216 | 0 | -6685.35 | -30164.457 | 15702 | 0 | 1849470 | 288759 | 7386.8492 | 0 | 10979.3984 | 46.3447 | 4121.2795 | 217.8498 | 5399.8596 | 7760.3031 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 28913.8 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0444 | 2456.4844 | 1515.3582 | 876.2457 | 1910.1671 | 0 | 0 | 1651.7814 | 3.0307 | 12042.6577 | 0 | 0 | 0 | 23970 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 25700
| 66 | Current | Current | 1CCAAB | 4/29/2025 9:19:05 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1837.453 | -1102.529 | 0 | -1368.584 | -2471.037 | -4668.903 | 834.556 | 468.014 | 1436.369 | 2024.216 | 0 | -6685.35 | -17079.023 | 15702 | 0 | 1905531 | 167943 | 7386.8492 | 0 | 10979.3984 | 26.8328 | 4136.242 | 176.7031 | 5561.0166 | 8871.303 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 18218.3 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 17.9829 | 1378.4504 | 737.3481 | 715.3515 | 2060.8019 | 0 | 0 | 1651.7814 | 3.0307 | 10634.0025 | 0 | 0 | 0 | 20510 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 20880
| 67 | Current | Current | 1CCABA | 4/29/2025 9:19:07 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1900.69 | -1105.744 | 0 | -1368.584 | -2576.319 | -4880.153 | 882.06 | 518.723 | 1261.226 | 2198.322 | 0 | -6971.159 | -31033.838 | 15783 | 0 | 1766889 | 296021 | 5731.5627 | 0 | 10979.3984 | 46.8157 | 4038.1464 | 204.5699 | 5402.0815 | 7702.5181 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 29740 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.041 | 2393.4401 | 1524.2115 | 874.0614 | 1839.2968 | 0 | 0 | 1651.7814 | 3.0307 | 11378.2721 | 0 | 0 | 0 | 24070 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 25790
| 68 | Current | Current | 1CCABB | 4/29/2025 9:19:09 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1900.69 | -1105.744 | 0 | -1368.584 | -2576.319 | -4880.153 | 882.06 | 518.723 | 1261.226 | 2198.322 | 0 | -6971.159 | -17944.574 | 15782 | 0 | 1823244 | 175892 | 5731.5627 | 0 | 10979.3984 | 28.4949 | 4058.1806 | 162.4334 | 5564.6036 | 8813.3883 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 19122.6 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18 | 1307.5869 | 646.1877 | 713.5597 | 1989.5118 | 0 | 0 | 1651.7814 | 3.0307 | 9961.1903 | 0 | 0 | 0 | 20630 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21000
| 69 | Current | Current | 1CCBAA | 4/29/2025 9:19:11 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1807.496 | -1098.121 | 0 | -1368.584 | -2032.107 | -4558.85 | 806.316 | 444.131 | 1376.565 | 1935.864 | 0 | -6302.284 | -29444.822 | 15562 | 0 | 1849572 | 282015 | 7386.8492 | 0 | 10979.3984 | 46.1024 | 4125.7676 | 220.0444 | 5385.4091 | 7770.5284 | 0 | 0 | 4524.3136 | 26.5495 | 0 | 0 | 0 | 28146.7 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.1058 | 2442.2182 | 1515.3582 | 874.0204 | 1915.2387 | 0 | 0 | 1651.7814 | 3.0307 | 12031.3676 | 0 | 0 | 0 | 23470 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 25190
| 70 | Current | Current | 1CCBAB | 4/29/2025 9:19:12 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1807.496 | -1098.121 | 0 | -1368.584 | -2032.107 | -4558.85 | 806.316 | 444.131 | 1376.565 | 1935.864 | 0 | -6302.284 | -16361.698 | 15561 | 0 | 1905603 | 160800 | 7386.8492 | 0 | 10979.3984 | 25.9249 | 4142.0133 | 178.4607 | 5545.8664 | 8881.4191 | 0 | 0 | 4524.3136 | 26.5495 | 0 | 0 | 0 | 17405.7 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.041 | 1365.3139 | 734.8191 | 712.7269 | 2065.9213 | 0 | 0 | 1651.7814 | 3.0307 | 10621.7704 | 0 | 0 | 0 | 20190 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 20550
| 71 | Current | Current | 1CCBBA | 4/29/2025 9:19:14 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1870.439 | -1101.627 | 0 | -1368.584 | -2119.507 | -4764.581 | 853.58 | 490.148 | 1209.543 | 2099.54 | 0 | -6571.928 | -30290.818 | 15634 | 0 | 1767537 | 290024 | 5731.5627 | 0 | 10979.3984 | 46.6519 | 4042.0543 | 206.2287 | 5401.2624 | 7712.1154 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 29057.7 | 0 | 0 | 3937 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0546 | 2380.4094 | 1506.2183 | 873.3173 | 1844.2319 | 0 | 0 | 1651.7814 | 3.0307 | 11370.1253 | 0 | 0 | 0 | 23690 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 25410
| 72 | Current | Current | 1CCBBB | 4/29/2025 9:19:16 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1870.439 | -1101.627 | 0 | -1368.584 | -2119.507 | -4764.581 | 853.58 | 490.148 | 1209.543 | 2099.54 | 0 | -6571.928 | -17203.277 | 15634 | 0 | 1823888 | 169368 | 5731.5627 | 0 | 10979.3984 | 27.5256 | 4063.4024 | 164.1433 | 5563.1565 | 8822.9686 | 0 | 0 | 4524.3102 | 26.5495 | 0 | 0 | 0 | 18380.4 | 0 | 0 | 887.8 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 17.9863 | 1293.8873 | 646.703 | 712.4266 | 1994.4674 | 0 | 0 | 1651.7814 | 3.0307 | 9952.5828 | 0 | 0 | 0 | 20320 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 20690
x | 73 | Current | Improved | 1AAAAA | 4/29/2025 9:16:54 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4649.082 | -1111.681 | 0 | -1368.584 | -3177.809 | -10021.72 | 1318.816 | 858.848 | 2408.691 | 3408.915 | 0 | -12333.6 | -32212.334 | 14894 | 0 | 1662998 | 293468 | 7386.8492 | 0 | 10979.3984 | 47.5256 | 3661.8802 | 171.4744 | 3494.7028 | 6080.962 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 29813.2 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0273 | 2407.5698 | 1543.2763 | 535.3105 | 1813.836 | 0 | 0 | 1651.7814 | 3.0307 | 11529.1356 | 0 | 0 | 0 | 27240 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 28960
| 74 | Current | Improved | 1AAAAB | 4/29/2025 9:16:56 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4649.082 | -1111.681 | 0 | -1368.584 | -3177.809 | -10021.72 | 1318.816 | 858.848 | 2408.691 | 3408.915 | 0 | -12333.6 | -20365.758 | 14890 | 0 | 1715219 | 188230 | 7386.8492 | 0 | 10979.3984 | 33.8055 | 3685.4058 | 137.1877 | 3659.5628 | 7083.1223 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 20608.7 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0512 | 1328.2217 | 660.6518 | 469.8396 | 1958.3514 | 0 | 0 | 1651.7814 | 3.0307 | 10177.0606 | 0 | 0 | 0 | 22970 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 23330
| 75 | Current | Improved | 1AAABA | 4/29/2025 9:16:57 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4807.696 | -1113.906 | 0 | -1368.584 | -3290.236 | -10403.42 | 1390.797 | 950.243 | 2061.176 | 3707.062 | 0 | -12874.56 | -33228.461 | 14988 | 0 | 1581018 | 302080 | 5731.5627 | 0 | 10979.3984 | 48.7474 | 3587.7983 | 161.0102 | 3490.3649 | 6030.3647 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 30792.9 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0239 | 2345.6005 | 1458.6142 | 532.9829 | 1746.7951 | 0 | 0 | 1651.7814 | 3.0307 | 10874.5179 | 0 | 0 | 0 | 27300 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 29020
| 76 | Current | Improved | 1AAABB | 4/29/2025 9:16:59 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4807.696 | -1113.906 | 0 | -1368.584 | -3290.236 | -10403.42 | 1390.797 | 950.243 | 2061.176 | 3707.062 | 0 | -12874.56 | -21380.381 | 14984 | 0 | 1633294 | 197043 | 5731.5627 | 0 | 10979.3984 | 35.2389 | 3611.9144 | 126.1263 | 3655.9758 | 7032.6922 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 21611.3 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0478 | 1264.1535 | 593.0682 | 469.1535 | 1891.5527 | 0 | 0 | 1651.7814 | 3.0307 | 9517.2108 | 0 | 0 | 0 | 23000 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 23360
| 77 | Current | Improved | 1AABAA | 4/29/2025 9:17:01 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4595.778 | -1108.99 | 0 | -1368.584 | -2647.677 | -9885.926 | 1291.173 | 828.067 | 2336.019 | 3307.493 | 0 | -11844.21 | -31483.686 | 14741 | 0 | 1663094 | 287462 | 7386.8492 | 0 | 10979.3984 | 47.157 | 3660.2284 | 172.6689 | 3493.1601 | 6085.4329 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 29129.9 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0683 | 2393.8394 | 1523.8053 | 534.7679 | 1822.4504 | 0 | 0 | 1651.7814 | 3.0307 | 11519.9615 | 0 | 0 | 0 | 26690 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 28340
| 78 | Current | Improved | 1AABAB | 4/29/2025 9:17:03 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4595.778 | -1108.99 | 0 | -1368.584 | -2647.677 | -9885.926 | 1291.173 | 828.067 | 2336.019 | 3307.493 | 0 | -11844.21 | -19637.393 | 14737 | 0 | 1715394 | 182006 | 7386.8492 | 0 | 10979.3984 | 33.0444 | 3686.4468 | 138.1229 | 3657.4673 | 7087.8219 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 19900.6 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0375 | 1314.6449 | 648.7133 | 469.4198 | 1966.9862 | 0 | 0 | 1651.7814 | 3.0307 | 10167.2551 | 0 | 0 | 0 | 22830 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 23190
| 79 | Current | Improved | 1AABBA | 4/29/2025 9:17:05 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4757.098 | -1111.448 | 0 | -1368.584 | -2743.786 | -10273.39 | 1361.822 | 918.716 | 2004.662 | 3602.113 | 0 | -12366.99 | -32489.775 | 14825 | 0 | 1580935 | 295886 | 5731.5627 | 0 | 10979.3984 | 48.0375 | 3584.9963 | 161.5665 | 3488.6755 | 6033.1531 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 30088.3 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0478 | 2332.7029 | 1441.034 | 532.4778 | 1755.0988 | 0 | 0 | 1651.7814 | 3.0307 | 10866.9957 | 0 | 0 | 0 | 27030 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 28750
| 80 | Current | Improved | 1AABBB | 4/29/2025 9:17:07 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4757.098 | -1111.448 | 0 | -1368.584 | -2743.786 | -10273.39 | 1361.822 | 918.716 | 2004.662 | 3602.113 | 0 | -12366.99 | -20641.926 | 14821 | 0 | 1633328 | 190879 | 5731.5627 | 0 | 10979.3984 | 34.587 | 3611.9314 | 126.8157 | 3653.7574 | 7035.5864 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 20910 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0341 | 1250.761 | 582.4368 | 468.7337 | 1899.8224 | 0 | 0 | 1651.7814 | 3.0307 | 9509.5419 | 0 | 0 | 0 | 22860 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 23230
| 81 | Current | Improved | 1ABAAA | 4/29/2025 9:17:09 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4309.447 | -1108.517 | 0 | -1368.584 | -2898.095 | -6715.244 | 1107.69 | 681.33 | 1973.182 | 2791.834 | 0 | -9845.851 | -29237.557 | 14632 | 0 | 1664883 | 268953 | 7386.8492 | 0 | 10979.3984 | 45.884 | 3675.4741 | 178.2764 | 3490.8495 | 6107.3135 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 27024.1 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0137 | 2410.9179 | 1547.2593 | 535.4914 | 1853.249 | 0 | 0 | 1651.7814 | 3.0307 | 11593.0332 | 0 | 0 | 0 | 25820 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27550
| 82 | Current | Improved | 1ABAAB | 4/29/2025 9:17:10 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4309.447 | -1108.517 | 0 | -1368.584 | -2898.095 | -6715.244 | 1107.69 | 681.33 | 1973.182 | 2791.834 | 0 | -9845.851 | -17393.246 | 14631 | 0 | 1717280 | 162841 | 7386.8492 | 0 | 10979.3984 | 31.0683 | 3706.4263 | 144.0341 | 3653.126 | 7109.4841 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 17720.3 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0512 | 1333.232 | 665.9488 | 468.4675 | 1998.0613 | 0 | 0 | 1651.7814 | 3.0307 | 10243.8763 | 0 | 0 | 0 | 22350 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22720
| 83 | Current | Improved | 1ABABA | 4/29/2025 9:17:12 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4495.643 | -1111.085 | 0 | -1368.584 | -3031.79 | -7048.75 | 1175.832 | 774.124 | 1735.96 | 3092.879 | 0 | -10277.06 | -30202.85 | 14704 | 0 | 1582327 | 276941 | 5731.5627 | 0 | 10979.3984 | 46.5665 | 3596.6516 | 166.2321 | 3486.027 | 6051.4125 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 27932.9 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0341 | 2348.6517 | 1462.7678 | 533.1501 | 1784.662 | 0 | 0 | 1651.7814 | 3.0307 | 10934.6203 | 0 | 0 | 0 | 25890 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27610
| 84 | Current | Improved | 1ABABB | 4/29/2025 9:17:14 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4495.643 | -1111.085 | 0 | -1368.584 | -3031.79 | -7048.75 | 1175.832 | 774.124 | 1735.96 | 3092.879 | 0 | -10277.06 | -18356.477 | 14704 | 0 | 1634879 | 171377 | 5731.5627 | 0 | 10979.3984 | 32.4027 | 3629.2215 | 131.645 | 3649.4195 | 7053.9209 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 18691.4 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0375 | 1267.3787 | 597.8941 | 467.7747 | 1929.2934 | 0 | 0 | 1651.7814 | 3.0307 | 9579.1937 | 0 | 0 | 0 | 22400 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22770
| 85 | Current | Improved | 1ABBAA | 4/29/2025 9:17:16 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4243.205 | -1104.798 | 0 | -1368.584 | -2400.513 | -6592.154 | 1079.972 | 649.019 | 1896.283 | 2684.943 | 0 | -9399.036 | -28507.744 | 14502 | 0 | 1665301 | 262964 | 7386.8492 | 0 | 10979.3984 | 45.628 | 3676.7915 | 179.7645 | 3489.3512 | 6115.4193 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 26342.8 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0785 | 2397.2114 | 1528.2763 | 535.0273 | 1862.133 | 0 | 0 | 1651.7814 | 3.0307 | 11583.8182 | 0 | 0 | 0 | 25560 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27280
| 86 | Current | Improved | 1ABBAB | 4/29/2025 9:17:18 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4243.205 | -1104.798 | 0 | -1368.584 | -2400.513 | -6592.154 | 1079.972 | 649.019 | 1896.283 | 2684.943 | 0 | -9399.036 | -16664.52 | 14498 | 0 | 1717712 | 156545 | 7386.8492 | 0 | 10979.3984 | 30.1843 | 3709.8154 | 145.1979 | 3650.829 | 7117.5489 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 17003.9 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0239 | 1320.4299 | 654.0136 | 468.017 | 2007.0374 | 0 | 0 | 1651.7814 | 3.0307 | 10233.9309 | 0 | 0 | 0 | 22120 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22490
| 87 | Current | Improved | 1ABBBA | 4/29/2025 9:17:20 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4422.426 | -1108.017 | 0 | -1368.584 | -2509.886 | -6912.568 | 1144.307 | 734.823 | 1667.032 | 2965.544 | 0 | -9809.775 | -29460.445 | 14556 | 0 | 1582581 | 270829 | 5731.5627 | 0 | 10979.3984 | 46.1672 | 3596.2113 | 167.4232 | 3484.4332 | 6058.2077 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 27237.6 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0853 | 2335.8257 | 1445.2149 | 532.6928 | 1793.2319 | 0 | 0 | 1651.7814 | 3.0307 | 10926.9547 | 0 | 0 | 0 | 25620 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27340
| 88 | Current | Improved | 1ABBBB | 4/29/2025 9:17:22 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4422.426 | -1108.017 | 0 | -1368.584 | -2509.886 | -6912.568 | 1144.307 | 734.823 | 1667.032 | 2965.544 | 0 | -9809.775 | -17614.766 | 14556 | 0 | 1635225 | 165123 | 5731.5627 | 0 | 10979.3984 | 31.8123 | 3631.9417 | 132.7372 | 3647.1806 | 7060.5387 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 17979.9 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0273 | 1253.9726 | 587.2696 | 467.331 | 1937.8394 | 0 | 0 | 1651.7814 | 3.0307 | 9571.221 | 0 | 0 | 0 | 22180 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22550
| 89 | Current | Improved | 1ACAAA | 4/29/2025 9:17:24 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4114.481 | -1106.279 | 0 | -1368.584 | -2740.485 | -5198.971 | 1001.451 | 596.498 | 1758.965 | 2485.545 | 0 | -8686.34 | -27761.533 | 14504 | 0 | 1666307 | 256817 | 7386.8492 | 0 | 10979.3984 | 45.2901 | 3686.754 | 182.488 | 3488.8291 | 6125.5968 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 25643.5 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0751 | 2412.7063 | 1549.877 | 535.6279 | 1873.7609 | 0 | 0 | 1651.7814 | 3.0307 | 11625.8728 | 0 | 0 | 0 | 25300 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27020
| 90 | Current | Improved | 1ACAAB | 4/29/2025 9:17:26 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4114.481 | -1106.279 | 0 | -1368.584 | -2740.485 | -5198.971 | 1001.451 | 596.498 | 1758.965 | 2485.545 | 0 | -8686.34 | -15919.185 | 14502 | 0 | 1718706 | 150071 | 7386.8492 | 0 | 10979.3984 | 29.3754 | 3720.4912 | 147.785 | 3649.7813 | 7127.9243 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 16267.5 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0068 | 1336.2593 | 668.6996 | 467.7337 | 2018.7814 | 0 | 0 | 1651.7814 | 3.0307 | 10278.2551 | 0 | 0 | 0 | 21900 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22270
| 91 | Current | Improved | 1ACABA | 4/29/2025 9:17:28 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4295.404 | -1109.318 | 0 | -1368.584 | -2870.131 | -5462.616 | 1060.205 | 676.467 | 1555.727 | 2751.975 | 0 | -9061.679 | -28695.498 | 14585 | 0 | 1583386 | 264592 | 5731.5627 | 0 | 10979.3984 | 45.9249 | 3603.7028 | 169.7986 | 3483.8564 | 6066.7777 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 26528.1 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0648 | 2350.3274 | 1465.0067 | 533.2491 | 1804.3753 | 0 | 0 | 1651.7814 | 3.0307 | 10965.5861 | 0 | 0 | 0 | 25370 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27090
| 92 | Current | Improved | 1ACABB | 4/29/2025 9:17:30 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4295.404 | -1109.318 | 0 | -1368.584 | -2870.131 | -5462.616 | 1060.205 | 676.467 | 1555.727 | 2751.975 | 0 | -9061.679 | -16850.723 | 14585 | 0 | 1636061 | 158560 | 5731.5627 | 0 | 10979.3984 | 31.0478 | 3641.1874 | 134.8839 | 3646.1533 | 7069.2042 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 17233.2 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0512 | 1269.1262 | 600.4368 | 467.0443 | 1948.9486 | 0 | 0 | 1651.7814 | 3.0307 | 9611.2688 | 0 | 0 | 0 | 21970 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22340
| 93 | Current | Improved | 1ACBAA | 4/29/2025 9:17:32 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4051.932 | -1102.444 | 0 | -1368.584 | -2267.498 | -5103.075 | 974.032 | 569.918 | 1694.583 | 2392.346 | 0 | -8262.652 | -27033.926 | 14359 | 0 | 1666936 | 250755 | 7386.8492 | 0 | 10979.3984 | 44.9556 | 3690.1157 | 183.942 | 3487.5014 | 6136.1974 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 24953.8 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0171 | 2398.9861 | 1530.7132 | 535.1672 | 1882.8394 | 0 | 0 | 1651.7814 | 3.0307 | 11616.5212 | 0 | 0 | 0 | 25000 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26720
| 94 | Current | Improved | 1ACBAB | 4/29/2025 9:17:34 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4051.932 | -1102.444 | 0 | -1368.584 | -2267.498 | -5103.075 | 974.032 | 569.918 | 1694.583 | 2392.346 | 0 | -8262.652 | -15192.77 | 14358 | 0 | 1719375 | 143755 | 7386.8492 | 0 | 10979.3984 | 28.57 | 3725.6652 | 149.4061 | 3647.713 | 7138.6274 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 15548.9 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0307 | 1323.4299 | 656.7679 | 467.1945 | 2027.9589 | 0 | 0 | 1651.7814 | 3.0307 | 10268.0606 | 0 | 0 | 0 | 21600 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21960
| 95 | Current | Improved | 1ACBBA | 4/29/2025 9:17:36 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4223.139 | -1105.568 | 0 | -1368.584 | -2371.898 | -5352.303 | 1031.065 | 641.732 | 1493.74 | 2636.707 | 0 | -8618.247 | -27953.461 | 14448 | 0 | 1583811 | 258519 | 5731.5627 | 0 | 10979.3984 | 45.5665 | 3605.0645 | 171.2218 | 3482.0646 | 6075.4637 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 25837.1 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0307 | 2337.5868 | 1447.5118 | 532.8122 | 1813.133 | 0 | 0 | 1651.7814 | 3.0307 | 10957.9718 | 0 | 0 | 0 | 25080 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26800
| 96 | Current | Improved | 1ACBBB | 4/29/2025 9:17:38 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4223.139 | -1105.568 | 0 | -1368.584 | -2371.898 | -5352.303 | 1031.065 | 641.732 | 1493.74 | 2636.707 | 0 | -8618.247 | -16109.539 | 14446 | 0 | 1636544 | 152142 | 5731.5627 | 0 | 10979.3984 | 30.157 | 3644.9724 | 136.1911 | 3643.7949 | 7077.955 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 16503 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.041 | 1255.7303 | 589.8532 | 466.4436 | 1957.6858 | 0 | 0 | 1651.7814 | 3.0307 | 9603.2825 | 0 | 0 | 0 | 21680 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22050
| 97 | Current | Improved | 1BAAAA | 4/29/2025 9:17:40 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2686.747 | -1110.092 | 0 | -1368.584 | -2999.972 | -9452.697 | 1203.151 | 729.658 | 2102.148 | 2990.746 | 0 | -10592.39 | -30123.699 | 14704 | 0 | 1663022 | 276303 | 7386.8492 | 0 | 10979.3984 | 46.4642 | 3662.7369 | 173.901 | 3492.5287 | 6081.4773 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 27860.3 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0444 | 2409.01 | 1544.6756 | 535.4368 | 1811.5118 | 0 | 0 | 1651.7814 | 3.0307 | 11533.2414 | 0 | 0 | 0 | 26060 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27780
| 98 | Current | Improved | 1BAAAB | 4/29/2025 9:17:42 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2686.747 | -1110.092 | 0 | -1368.584 | -2999.972 | -9452.697 | 1203.151 | 729.658 | 2102.148 | 2990.746 | 0 | -10592.39 | -18277.98 | 14703 | 0 | 1715333 | 170435 | 7386.8492 | 0 | 10979.3984 | 32.0341 | 3690.5458 | 139.2969 | 3655.8359 | 7083.8492 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 18584.2 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0307 | 1330.3958 | 663.2866 | 468.6655 | 1956.034 | 0 | 0 | 1651.7814 | 3.0307 | 10181.1493 | 0 | 0 | 0 | 22540 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22900
| 99 | Current | Improved | 1BAABA | 4/29/2025 9:17:44 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2787.15 | -1112.567 | 0 | -1368.584 | -3133.969 | -9907.344 | 1276.18 | 828.088 | 1841.14 | 3306.102 | 0 | -11058.11 | -31116.422 | 14787 | 0 | 1580816 | 284497 | 5731.5627 | 0 | 10979.3984 | 47.3072 | 3587.2864 | 162.058 | 3488.0748 | 6029.1497 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 28792.5 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0273 | 2346.2455 | 1459.4879 | 533.0921 | 1744.0135 | 0 | 0 | 1651.7814 | 3.0307 | 10876.8182 | 0 | 0 | 0 | 26120 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27840
| 100 | Current | Improved | 1BAABB | 4/29/2025 9:17:46 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2787.15 | -1112.567 | 0 | -1368.584 | -3133.969 | -9907.344 | 1276.18 | 828.088 | 1841.14 | 3306.102 | 0 | -11058.11 | -19269.012 | 14785 | 0 | 1633212 | 179243 | 5731.5627 | 0 | 10979.3984 | 33.43 | 3615.5901 | 127.4437 | 3652.1499 | 7031.5318 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 19586.3 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.041 | 1264.8941 | 595.116 | 467.9795 | 1888.7951 | 0 | 0 | 1651.7814 | 3.0307 | 9519.378 | 0 | 0 | 0 | 22580 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22950
| 101 | Current | Improved | 1BABAA | 4/29/2025 9:17:48 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2650.875 | -1106.92 | 0 | -1368.584 | -2489.491 | -9285.394 | 1174.579 | 695.408 | 2021.372 | 2878.022 | 0 | -10131.88 | -29389.92 | 14568 | 0 | 1663113 | 270266 | 7386.8492 | 0 | 10979.3984 | 46.0683 | 3660.9826 | 174.8669 | 3490.8803 | 6086.2998 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 27173.5 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0341 | 2395.2421 | 1525.7337 | 534.8907 | 1820.1534 | 0 | 0 | 1651.7814 | 3.0307 | 11524.0912 | 0 | 0 | 0 | 25800 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27520
| 102 | Current | Improved | 1BABAB | 4/29/2025 9:17:50 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2650.875 | -1106.92 | 0 | -1368.584 | -2489.491 | -9285.394 | 1174.579 | 695.408 | 2021.372 | 2878.022 | 0 | -10131.88 | -17544.838 | 14567 | 0 | 1715533 | 164211 | 7386.8492 | 0 | 10979.3984 | 31.4471 | 3691.8905 | 140.372 | 3653.597 | 7088.6274 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 17876.1 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0137 | 1317.5289 | 651.3378 | 468.2457 | 1964.6756 | 0 | 0 | 1651.7814 | 3.0307 | 10171.3541 | 0 | 0 | 0 | 22340 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22710
| 103 | Current | Improved | 1BABBA | 4/29/2025 9:17:52 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2750.431 | -1109.786 | 0 | -1368.584 | -2601.236 | -9733.007 | 1244.313 | 789.069 | 1772.734 | 3180.707 | 0 | -10576.22 | -30370.984 | 14642 | 0 | 1580829 | 278395 | 5731.5627 | 0 | 10979.3984 | 46.8191 | 3584.9417 | 162.9829 | 3486.3683 | 6033.0063 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 28098.4 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0034 | 2333.5664 | 1441.9214 | 532.587 | 1752.3036 | 0 | 0 | 1651.7814 | 3.0307 | 10869.2653 | 0 | 0 | 0 | 25860 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27580
| 104 | Current | Improved | 1BABBB | 4/29/2025 9:17:54 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2750.431 | -1109.786 | 0 | -1368.584 | -2601.236 | -9733.007 | 1244.313 | 789.069 | 1772.734 | 3180.707 | 0 | -10576.22 | -18524.027 | 14641 | 0 | 1633331 | 172876 | 5731.5627 | 0 | 10979.3984 | 32.802 | 3616.4297 | 128.2662 | 3649.9178 | 7035.3441 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 18861.9 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0512 | 1251.447 | 584.4778 | 467.5563 | 1897.0408 | 0 | 0 | 1651.7814 | 3.0307 | 9511.6989 | 0 | 0 | 0 | 22390 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22760
| 105 | Current | Improved | 1BBAAA | 4/29/2025 9:17:56 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2487.478 | -1105.918 | 0 | -1368.584 | -2699.953 | -6244.541 | 988.083 | 567.608 | 1692.615 | 2400.977 | 0 | -8257.193 | -27157.793 | 14453 | 0 | 1665334 | 251869 | 7386.8492 | 0 | 10979.3984 | 45.157 | 3680.5458 | 181.802 | 3488.6516 | 6111.5046 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 25080.6 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0717 | 2412.307 | 1549.191 | 535.6245 | 1851.1841 | 0 | 0 | 1651.7814 | 3.0307 | 11597.8182 | 0 | 0 | 0 | 25020 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26740
| 106 | Current | Improved | 1BBAAB | 4/29/2025 9:17:58 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2487.478 | -1105.918 | 0 | -1368.584 | -2699.953 | -6244.541 | 988.083 | 567.608 | 1692.615 | 2400.977 | 0 | -8257.193 | -15315.666 | 14451 | 0 | 1717711 | 144889 | 7386.8492 | 0 | 10979.3984 | 28.9352 | 3714.9587 | 146.7543 | 3649.1601 | 7113.7639 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 15677.9 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0273 | 1336.1774 | 668.5665 | 467.0887 | 1995.9828 | 0 | 0 | 1651.7814 | 3.0307 | 10248.6988 | 0 | 0 | 0 | 21650 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22020
| 107 | Current | Improved | 1BBABA | 4/29/2025 9:18:00 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2576.924 | -1109.172 | 0 | -1368.584 | -2817.203 | -6532.413 | 1045.754 | 633.641 | 1483.308 | 2629.841 | 0 | -8611.753 | -28088.584 | 14531 | 0 | 1582434 | 259739 | 5731.5627 | 0 | 10979.3984 | 45.8669 | 3597.6755 | 168.5426 | 3483.4263 | 6053.7265 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 25975.9 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0546 | 2349.324 | 1463.5323 | 533.2593 | 1782.0647 | 0 | 0 | 1651.7814 | 3.0307 | 10937.5281 | 0 | 0 | 0 | 25100 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26820
| 108 | Current | Improved | 1BBABB | 4/29/2025 9:18:02 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2576.924 | -1109.172 | 0 | -1368.584 | -2817.203 | -6532.413 | 1045.754 | 633.641 | 1483.308 | 2629.841 | 0 | -8611.753 | -16243.719 | 14529 | 0 | 1635138 | 153331 | 5731.5627 | 0 | 10979.3984 | 30.57 | 3635.9383 | 134.0546 | 3645.5492 | 7056.2247 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 16638.3 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 17.9932 | 1268.0067 | 599.8771 | 466.4471 | 1926.7029 | 0 | 0 | 1651.7814 | 3.0307 | 9581.9753 | 0 | 0 | 0 | 21730 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22100
| 109 | Current | Improved | 1BBBAA | 4/29/2025 9:18:04 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2453.632 | -1102.213 | 0 | -1368.584 | -2235.824 | -6131.729 | 961.294 | 543.122 | 1633.018 | 2314.471 | 0 | -7840.077 | -26427.414 | 14305 | 0 | 1665764 | 245761 | 7386.8492 | 0 | 10979.3984 | 44.8293 | 3681.9041 | 182.8566 | 3487.2284 | 6120.2623 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 24385.7 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0512 | 2398.5732 | 1529.7064 | 535.1638 | 1860.0715 | 0 | 0 | 1651.7814 | 3.0307 | 11588.5622 | 0 | 0 | 0 | 24700 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26420
| 110 | Current | Improved | 1BBBAB | 4/29/2025 9:18:06 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2453.632 | -1102.213 | 0 | -1368.584 | -2235.824 | -6131.729 | 961.294 | 543.122 | 1633.018 | 2314.471 | 0 | -7840.077 | -14586.651 | 14304 | 0 | 1718244 | 138467 | 7386.8492 | 0 | 10979.3984 | 28.0273 | 3719.0304 | 148.2833 | 3647.3273 | 7122.5489 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 14947.3 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.041 | 1323.3207 | 656.6006 | 466.2832 | 2004.9589 | 0 | 0 | 1651.7814 | 3.0307 | 10238.6681 | 0 | 0 | 0 | 21290 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21660
| 111 | Current | Improved | 1BBBBA | 4/29/2025 9:18:08 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2537.231 | -1105.255 | 0 | -1368.584 | -2328.202 | -6398.494 | 1015.841 | 601.014 | 1424.397 | 2518.798 | 0 | -8177.714 | -27341.266 | 14383 | 0 | 1582897 | 253522 | 5731.5627 | 0 | 10979.3984 | 45.5597 | 3599.5253 | 170.0068 | 3481.7028 | 6062.5729 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 25268.7 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0785 | 2336.7165 | 1446.0101 | 532.8157 | 1790.6278 | 0 | 0 | 1651.7814 | 3.0307 | 10929.8592 | 0 | 0 | 0 | 24790 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26510
| 112 | Current | Improved | 1BBBBB | 4/29/2025 9:18:10 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2537.231 | -1105.255 | 0 | -1368.584 | -2328.202 | -6398.494 | 1015.841 | 601.014 | 1424.397 | 2518.798 | 0 | -8177.714 | -15497.532 | 14383 | 0 | 1635617 | 146856 | 5731.5627 | 0 | 10979.3984 | 29.6382 | 3639.9007 | 135.3686 | 3643.1021 | 7064.7469 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 15901.6 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0785 | 1254.5528 | 589.2389 | 465.6518 | 1935.2422 | 0 | 0 | 1651.7814 | 3.0307 | 9573.9617 | 0 | 0 | 0 | 21390 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21760
| 113 | Current | Improved | 1BCAAA | 4/29/2025 9:18:12 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2379.674 | -1103.608 | 0 | -1368.584 | -2542.453 | -4809.708 | 875.353 | 499.181 | 1514.865 | 2137.203 | 0 | -7177.425 | -25696.594 | 14321 | 0 | 1666839 | 239789 | 7386.8492 | 0 | 10979.3984 | 44.6587 | 3692.6072 | 185.8908 | 3486.9997 | 6130.4398 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 23706.3 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0512 | 2414.0954 | 1551.3753 | 535.7645 | 1871.836 | 0 | 0 | 1651.7814 | 3.0307 | 11631.0298 | 0 | 0 | 0 | 24370 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26090
| 114 | Current | Improved | 1BCAAB | 4/29/2025 9:18:14 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2379.674 | -1103.608 | 0 | -1368.584 | -2542.453 | -4809.708 | 875.353 | 499.181 | 1514.865 | 2137.203 | 0 | -7177.425 | -13857.492 | 14319 | 0 | 1719246 | 131987 | 7386.8492 | 0 | 10979.3984 | 27.0717 | 3729.6311 | 151.2696 | 3646.5389 | 7132.6513 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 14210.1 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0444 | 1339.2524 | 680.1057 | 465.3856 | 2016.8394 | 0 | 0 | 1651.7814 | 3.0307 | 10283.552 | 0 | 0 | 0 | 20940 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21310
| 115 | Current | Improved | 1BCABA | 4/29/2025 9:18:16 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2466.026 | -1106.774 | 0 | -1368.584 | -2650.19 | -5027.251 | 925.345 | 554.594 | 1328.401 | 2325.755 | 0 | -7484.73 | -26586.652 | 14393 | 0 | 1583765 | 247303 | 5731.5627 | 0 | 10979.3984 | 45.2355 | 3607.9929 | 172.1638 | 3481.0304 | 6071.9142 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 24561.1 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0171 | 2351.0783 | 1465.9555 | 533.372 | 1801.9452 | 0 | 0 | 1651.7814 | 3.0307 | 10968.8216 | 0 | 0 | 0 | 24460 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26180
| 116 | Current | Improved | 1BCABB | 4/29/2025 9:18:18 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2466.026 | -1106.774 | 0 | -1368.584 | -2650.19 | -5027.251 | 925.345 | 554.594 | 1328.401 | 2325.755 | 0 | -7484.73 | -14744.101 | 14392 | 0 | 1636507 | 140173 | 5731.5627 | 0 | 10979.3984 | 28.7509 | 3650.0338 | 137.3174 | 3642.0133 | 7074.1359 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 15141.4 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0717 | 1269.761 | 602.4914 | 464.8293 | 1946.5186 | 0 | 0 | 1651.7814 | 3.0307 | 9614.4326 | 0 | 0 | 0 | 21050 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21420
| 117 | Current | Improved | 1BCBAA | 4/29/2025 9:18:20 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2340.72 | -1099.367 | 0 | -1368.584 | -2093.955 | -4702.761 | 846.968 | 474.036 | 1453.507 | 2047.615 | 0 | -6783.262 | -24974.375 | 14170 | 0 | 1667400 | 233899 | 7386.8492 | 0 | 10979.3984 | 44.471 | 3694.7096 | 187.1945 | 3485.7437 | 6140.7572 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 23036.2 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0512 | 2400.3889 | 1531.9248 | 535.3037 | 1880.9828 | 0 | 0 | 1651.7814 | 3.0307 | 11621.8113 | 0 | 0 | 0 | 23990 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 25710
| 118 | Current | Improved | 1BCBAB | 4/29/2025 9:18:22 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2340.72 | -1099.367 | 0 | -1368.584 | -2093.955 | -4702.761 | 846.968 | 474.036 | 1453.507 | 2047.615 | 0 | -6783.262 | -13137.049 | 14170 | 0 | 1719851 | 125674 | 7386.8492 | 0 | 10979.3984 | 26.1809 | 3733.771 | 152.8362 | 3644.399 | 7143.1974 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 13491.9 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0341 | 1326.4094 | 677.6689 | 464.1535 | 2026.0817 | 0 | 0 | 1651.7814 | 3.0307 | 10273.4189 | 0 | 0 | 0 | 20500 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 20860
| 119 | Current | Improved | 1BCBBA | 4/29/2025 9:18:24 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2426.571 | -1102.708 | 0 | -1368.584 | -2185.182 | -4918.819 | 895.932 | 526.389 | 1277.256 | 2228.199 | 0 | -7074.087 | -25842.301 | 14229 | 0 | 1584273 | 241137 | 5731.5627 | 0 | 10979.3984 | 44.9147 | 3609.6721 | 173.8362 | 3479.4161 | 6081.6445 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 23859.7 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0307 | 2338.5425 | 1448.2627 | 532.9351 | 1810.7848 | 0 | 0 | 1651.7814 | 3.0307 | 10961.3336 | 0 | 0 | 0 | 24090 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 25810
| 120 | Current | Improved | 1BCBBB | 4/29/2025 9:18:27 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2426.571 | -1102.708 | 0 | -1368.584 | -2185.182 | -4918.819 | 895.932 | 526.389 | 1277.256 | 2228.199 | 0 | -7074.087 | -14000.962 | 14228 | 0 | 1637068 | 133599 | 5731.5627 | 0 | 10979.3984 | 27.7782 | 3654.0475 | 138.843 | 3639.8427 | 7084.0131 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 14393.5 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0137 | 1256.3787 | 593.0853 | 463.587 | 1955.3377 | 0 | 0 | 1651.7814 | 3.0307 | 9606.5146 | 0 | 0 | 0 | 20610 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 20980
| 121 | Current | Improved | 1CAAAA | 4/29/2025 9:18:29 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2061.734 | -1109.454 | 0 | -1368.584 | -2933.382 | -9236.546 | 1162.833 | 685.568 | 1996.693 | 2846.548 | 0 | -10018.06 | -29404.658 | 14655 | 0 | 1662928 | 270416 | 7386.8492 | 0 | 10979.3984 | 46.1536 | 3661.8222 | 174.587 | 3491.614 | 6080.8527 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 27190.6 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0375 | 2409.4059 | 1545.1603 | 535.4744 | 1811.8667 | 0 | 0 | 1651.7814 | 3.0307 | 11534.1151 | 0 | 0 | 0 | 25810 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27530
| 122 | Current | Improved | 1CAAAB | 4/29/2025 9:18:31 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2061.734 | -1109.454 | 0 | -1368.584 | -2933.382 | -9236.546 | 1162.833 | 685.568 | 1996.693 | 2846.548 | 0 | -10018.06 | -17559.387 | 14652 | 0 | 1715291 | 164330 | 7386.8492 | 0 | 10979.3984 | 31.5802 | 3691.457 | 140.0853 | 3654.4331 | 7083.0677 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 17889.6 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0887 | 1331.191 | 663.9965 | 468.2662 | 1955.1125 | 0 | 0 | 1651.7814 | 3.0307 | 10181.9889 | 0 | 0 | 0 | 22360 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22720
| 123 | Current | Improved | 1CAABA | 4/29/2025 9:18:33 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2132.7 | -1112.068 | 0 | -1368.584 | -3066.541 | -9686.394 | 1232.179 | 778.36 | 1753.213 | 3146.58 | 0 | -10455.95 | -30387.85 | 14719 | 0 | 1580737 | 278587 | 5731.5627 | 0 | 10979.3984 | 46.9522 | 3586.6072 | 162.7474 | 3487.126 | 6028.6821 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 28120.1 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0307 | 2346.4162 | 1459.8122 | 533.1228 | 1743.9555 | 0 | 0 | 1651.7814 | 3.0307 | 10877.0537 | 0 | 0 | 0 | 25870 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27600
| 124 | Current | Improved | 1CAABB | 4/29/2025 9:18:35 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2132.7 | -1112.068 | 0 | -1368.584 | -3066.541 | -9686.394 | 1232.179 | 778.36 | 1753.213 | 3146.58 | 0 | -10455.95 | -18540.818 | 14718 | 0 | 1633181 | 173074 | 5731.5627 | 0 | 10979.3984 | 32.9249 | 3616.7813 | 128.0239 | 3650.8154 | 7030.9209 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 18884.5 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0068 | 1265.017 | 595.6006 | 467.5768 | 1887.7132 | 0 | 0 | 1651.7814 | 3.0307 | 9519.5419 | 0 | 0 | 0 | 22410 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22770
| 125 | Current | Improved | 1CABAA | 4/29/2025 9:18:37 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2035.671 | -1105.962 | 0 | -1368.584 | -2432.857 | -9069.122 | 1132.89 | 652.866 | 1919.648 | 2738.887 | 0 | -9567.904 | -28669.217 | 14514 | 0 | 1663173 | 264407 | 7386.8492 | 0 | 10979.3984 | 45.8771 | 3661.8188 | 175.6996 | 3489.9041 | 6087.0848 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 26507 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0717 | 2395.6346 | 1525.778 | 534.9283 | 1820.051 | 0 | 0 | 1651.7814 | 3.0307 | 11524.9376 | 0 | 0 | 0 | 25540 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27260
| 126 | Current | Improved | 1CABAB | 4/29/2025 9:18:39 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2035.671 | -1105.962 | 0 | -1368.584 | -2432.857 | -9069.122 | 1132.89 | 652.866 | 1919.648 | 2738.887 | 0 | -9567.904 | -16824.814 | 14512 | 0 | 1715587 | 157953 | 7386.8492 | 0 | 10979.3984 | 30.6007 | 3693.986 | 141.0751 | 3652.2966 | 7089.1325 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 17164.2 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 17.9488 | 1318.3139 | 652.0102 | 467.8566 | 1963.7541 | 0 | 0 | 1651.7814 | 3.0307 | 10172.2108 | 0 | 0 | 0 | 22130 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22500
| 127 | Current | Improved | 1CABBA | 4/29/2025 9:18:41 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2106.267 | -1109.082 | 0 | -1368.584 | -2542.893 | -9507.826 | 1201.892 | 739.842 | 1685.911 | 3022.081 | 0 | -9984.928 | -29639.732 | 14579 | 0 | 1580824 | 272472 | 5731.5627 | 0 | 10979.3984 | 46.5017 | 3585.0065 | 163.7577 | 3485.4844 | 6033.2794 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 27424.5 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0273 | 2333.795 | 1442.2797 | 532.6177 | 1751.7302 | 0 | 0 | 1651.7814 | 3.0307 | 10869.5281 | 0 | 0 | 0 | 25610 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 27330
| 128 | Current | Improved | 1CABBB | 4/29/2025 9:18:43 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2106.267 | -1109.082 | 0 | -1368.584 | -2542.893 | -9507.826 | 1201.892 | 739.842 | 1685.911 | 3022.081 | 0 | -9984.928 | -17793.205 | 14578 | 0 | 1633367 | 166702 | 5731.5627 | 0 | 10979.3984 | 32.2082 | 3618.1806 | 128.942 | 3648.655 | 7035.566 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 18159.4 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0512 | 1251.5664 | 584.9317 | 467.1399 | 1895.9657 | 0 | 0 | 1651.7814 | 3.0307 | 9511.8593 | 0 | 0 | 0 | 22190 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 22560
| 129 | Current | Improved | 1CBAAA | 4/29/2025 9:18:45 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1919.807 | -1105.069 | 0 | -1368.584 | -2635.786 | -6090.363 | 944.852 | 536.355 | 1614.435 | 2288.108 | 0 | -7735.858 | -26445.143 | 14391 | 0 | 1665373 | 245908 | 7386.8492 | 0 | 10979.3984 | 44.9113 | 3681.2693 | 182.4095 | 3487.8632 | 6112.0882 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 24402.4 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0546 | 2412.6756 | 1549.3309 | 535.6621 | 1851.2183 | 0 | 0 | 1651.7814 | 3.0307 | 11598.7977 | 0 | 0 | 0 | 24710 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26430
| 130 | Current | Improved | 1CBAAB | 4/29/2025 9:18:47 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1919.807 | -1105.069 | 0 | -1368.584 | -2635.786 | -6090.363 | 944.852 | 536.355 | 1614.435 | 2288.108 | 0 | -7735.858 | -14604.075 | 14389 | 0 | 1717811 | 138583 | 7386.8492 | 0 | 10979.3984 | 28.0717 | 3717.4502 | 147.8293 | 3648.0714 | 7114.3373 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 14960.6 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 17.9966 | 1336.9555 | 669.2798 | 466.2696 | 1995.1329 | 0 | 0 | 1651.7814 | 3.0307 | 10249.6476 | 0 | 0 | 0 | 21320 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21690
| 131 | Current | Improved | 1CBABA | 4/29/2025 9:18:49 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1980.672 | -1108.276 | 0 | -1368.584 | -2743.472 | -6354.567 | 999.919 | 592.936 | 1407.051 | 2487.569 | 0 | -8068.097 | -27360.709 | 14465 | 0 | 1582524 | 253730 | 5731.5627 | 0 | 10979.3984 | 45.645 | 3598.9076 | 169.1263 | 3482.4161 | 6055.0951 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 25292.3 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0205 | 2349.5356 | 1463.7098 | 533.2901 | 1781.4538 | 0 | 0 | 1651.7814 | 3.0307 | 10937.9547 | 0 | 0 | 0 | 24790 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26510
| 132 | Current | Improved | 1CBABB | 4/29/2025 9:18:51 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1980.672 | -1108.276 | 0 | -1368.584 | -2743.472 | -6354.567 | 999.919 | 592.936 | 1407.051 | 2487.569 | 0 | -8068.097 | -15516.529 | 14463 | 0 | 1635259 | 147013 | 5731.5627 | 0 | 10979.3984 | 29.7611 | 3638.7096 | 134.9488 | 3644.0031 | 7057.525 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 15919.6 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0375 | 1268.1159 | 600.3515 | 465.6416 | 1925.6927 | 0 | 0 | 1651.7814 | 3.0307 | 9582.3371 | 0 | 0 | 0 | 21420 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21780
| 133 | Current | Improved | 1CBBAA | 4/29/2025 9:18:52 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1890.967 | -1101.033 | 0 | -1368.584 | -2175.514 | -5960.703 | 915.144 | 509.034 | 1549.085 | 2194.663 | 0 | -7328.874 | -25715.549 | 14242 | 0 | 1665885 | 239939 | 7386.8492 | 0 | 10979.3984 | 44.6519 | 3683.1055 | 184.1536 | 3486.5253 | 6121.3135 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 23723.4 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0307 | 2398.9452 | 1530.0067 | 535.2013 | 1860.3446 | 0 | 0 | 1651.7814 | 3.0307 | 11589.6475 | 0 | 0 | 0 | 24360 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26080
| 134 | Current | Improved | 1CBBAB | 4/29/2025 9:18:54 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1890.967 | -1101.033 | 0 | -1368.584 | -2175.514 | -5960.703 | 915.144 | 509.034 | 1549.085 | 2194.663 | 0 | -7328.874 | -13876.086 | 14242 | 0 | 1718353 | 132185 | 7386.8492 | 0 | 10979.3984 | 27.1604 | 3721.3444 | 149.4266 | 3646.1942 | 7123.5011 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 14232.7 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0512 | 1324.1091 | 663.0375 | 465.1638 | 2004.1398 | 0 | 0 | 1651.7814 | 3.0307 | 10239.7739 | 0 | 0 | 0 | 20920 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21280
| 135 | Current | Improved | 1CBBBA | 4/29/2025 9:18:56 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1953.508 | -1104.263 | 0 | -1368.584 | -2267.42 | -6226.989 | 968.362 | 564.539 | 1355.358 | 2387.511 | 0 | -7644.995 | -26612.596 | 14316 | 0 | 1582943 | 247516 | 5731.5627 | 0 | 10979.3984 | 45.256 | 3599.9383 | 170.6348 | 3480.655 | 6063.8937 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 24585.4 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0171 | 2336.9384 | 1446.0579 | 532.8498 | 1790.2217 | 0 | 0 | 1651.7814 | 3.0307 | 10930.4018 | 0 | 0 | 0 | 24450 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 26170
| 136 | Current | Improved | 1CBBBB | 4/29/2025 9:18:58 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1953.508 | -1104.263 | 0 | -1368.584 | -2267.42 | -6226.989 | 968.362 | 564.539 | 1355.358 | 2387.511 | 0 | -7644.995 | -14769.745 | 14313 | 0 | 1635729 | 140413 | 5731.5627 | 0 | 10979.3984 | 28.7816 | 3642.5014 | 136.116 | 3641.6482 | 7066.1632 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 15168.7 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0648 | 1254.6723 | 589.7508 | 464.6075 | 1934.2626 | 0 | 0 | 1651.7814 | 3.0307 | 9574.4156 | 0 | 0 | 0 | 21030 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21390
| 137 | Current | Improved | 1CCAAA | 4/29/2025 9:19:00 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1837.453 | -1102.529 | 0 | -1368.584 | -2471.037 | -4668.903 | 834.556 | 468.014 | 1436.369 | 2024.216 | 0 | -6685.35 | -24993.053 | 14239 | 0 | 1666896 | 234049 | 7386.8492 | 0 | 10979.3984 | 44.5051 | 3693.1533 | 186.843 | 3486.3376 | 6131.0268 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 23053.2 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0239 | 2414.4947 | 1551.8702 | 535.8054 | 1872.3343 | 0 | 0 | 1651.7814 | 3.0307 | 11632.2891 | 0 | 0 | 0 | 24000 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 25720
| 138 | Current | Improved | 1CCAAB | 4/29/2025 9:19:02 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1837.453 | -1102.529 | 0 | -1368.584 | -2471.037 | -4668.903 | 834.556 | 468.014 | 1436.369 | 2024.216 | 0 | -6685.35 | -13155.267 | 14240 | 0 | 1719325 | 125804 | 7386.8492 | 0 | 10979.3984 | 26.2389 | 3731.7983 | 152.0853 | 3645.225 | 7133.525 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 13506.7 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0137 | 1340.0681 | 691.9351 | 464.1092 | 2016.0681 | 0 | 0 | 1651.7814 | 3.0307 | 10284.7568 | 0 | 0 | 0 | 20530 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 20900
| 139 | Current | Improved | 1CCABA | 4/29/2025 9:19:04 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1900.69 | -1105.744 | 0 | -1368.584 | -2576.319 | -4880.153 | 882.06 | 518.723 | 1261.226 | 2198.322 | 0 | -6971.159 | -25862.498 | 14320 | 0 | 1583877 | 241334 | 5731.5627 | 0 | 10979.3984 | 45.0136 | 3608.9485 | 173.3379 | 3480.2318 | 6073.2657 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 23882.1 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0478 | 2351.3138 | 1466.0204 | 533.4061 | 1801.8019 | 0 | 0 | 1651.7814 | 3.0307 | 10969.5144 | 0 | 0 | 0 | 24100 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 25820
| 140 | Current | Improved | 1CCABB | 4/29/2025 9:19:06 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1900.69 | -1105.744 | 0 | -1368.584 | -2576.319 | -4880.153 | 882.06 | 518.723 | 1261.226 | 2198.322 | 0 | -6971.159 | -14020.812 | 14320 | 0 | 1636642 | 133785 | 5731.5627 | 0 | 10979.3984 | 27.9283 | 3652.7198 | 138.1433 | 3640.8154 | 7075.6137 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 14414.6 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0375 | 1269.8941 | 603.9453 | 463.5426 | 1945.5766 | 0 | 0 | 1651.7814 | 3.0307 | 9615.006 | 0 | 0 | 0 | 20650 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 21010
| 141 | Current | Improved | 1CCBAA | 4/29/2025 9:19:08 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1807.496 | -1098.121 | 0 | -1368.584 | -2032.107 | -4558.85 | 806.316 | 444.131 | 1376.565 | 1935.864 | 0 | -6302.284 | -24274.299 | 14100 | 0 | 1666702 | 227855 | 7386.8492 | 0 | 10979.3984 | 44.2662 | 3694.713 | 188.1775 | 3469.2079 | 6141.2452 | 0 | 0 | 4533.7266 | 26.5495 | 0 | 0 | 0 | 22348.6 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0171 | 2400.8018 | 1532.5903 | 533.7201 | 1881.8463 | 0 | 0 | 1651.7814 | 3.0307 | 11621.4803 | 0 | 0 | 0 | 23500 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 25220
| 142 | Current | Improved | 1CCBAB | 4/29/2025 9:19:10 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1807.496 | -1098.121 | 0 | -1368.584 | -2032.107 | -4558.85 | 806.316 | 444.131 | 1376.565 | 1935.864 | 0 | -6302.284 | -12438.797 | 14100 | 0 | 1719198 | 119196 | 7386.8492 | 0 | 10979.3984 | 25.314 | 3735.2522 | 153.6792 | 3628.1772 | 7143.6581 | 0 | 0 | 4533.7266 | 26.5495 | 0 | 0 | 0 | 12754.9 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 18.0375 | 1327.232 | 689.546 | 460.9692 | 2025.348 | 0 | 0 | 1651.7814 | 3.0307 | 10273.1186 | 0 | 0 | 0 | 20210 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 20580
| 143 | Current | Improved | 1CCBBA | 4/29/2025 9:19:11 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1870.439 | -1101.627 | 0 | -1368.584 | -2119.507 | -4764.581 | 853.58 | 490.148 | 1209.543 | 2099.54 | 0 | -6571.928 | -25119.48 | 14171 | 0 | 1584349 | 235317 | 5731.5627 | 0 | 10979.3984 | 44.8089 | 3609.9656 | 174.8464 | 3478.6448 | 6082.863 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 23197.6 | 0 | 0 | 3573.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0307 | 2338.7711 | 1448.6176 | 532.9727 | 1811.2115 | 0 | 0 | 1651.7814 | 3.0307 | 10961.9513 | 0 | 0 | 0 | 23710 | 0 | 0 | 2130 | 0 | 0 | 0 | 0 | 0 | 25480
| 144 | Current | Improved | 1CCBBB | 4/29/2025 9:19:13 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1870.439 | -1101.627 | 0 | -1368.584 | -2119.507 | -4764.581 | 853.58 | 490.148 | 1209.543 | 2099.54 | 0 | -6571.928 | -13279.52 | 14172 | 0 | 1637154 | 127260 | 5731.5627 | 0 | 10979.3984 | 26.9659 | 3655.8188 | 139.6928 | 3638.7164 | 7085.2042 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 13672.3 | 0 | 0 | 805.5 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 18.0205 | 1256.505 | 604.389 | 462.3481 | 1954.423 | 0 | 0 | 1651.7814 | 3.0307 | 9607.0982 | 0 | 0 | 0 | 20350 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 20720
x | 145 | ASHP | Improved | 1AAAAA | 4/29/2025 9:17:02 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4649.082 | -1111.681 | 0 | -1368.584 | -3177.809 | -10021.72 | 1318.816 | 858.848 | 2408.691 | 3408.915 | 0 | -12333.6 | -31414.166 | 18888 | 17 | 2144127 | 75792 | 7386.8492 | 0 | 10979.3984 | 10468.7295 | 3885.3819 | 92.5461 | 3439.0065 | 6097.0234 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8622.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.4434 | 1448.0442 | 870.5665 | 480.2013 | 1849.2729 | 0 | 0 | 1651.7814 | 3.0307 | 12865.5211 | 0 | 0 | 0 | 33210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33210
| 146 | ASHP | Improved | 1AAAAB | 4/29/2025 9:17:04 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4649.082 | -1111.681 | 0 | -1368.584 | -3177.809 | -10021.72 | 1318.816 | 858.848 | 2408.691 | 3408.915 | 0 | -12333.6 | -20375.576 | 15171 | 0 | 2013841 | 56650 | 7386.8492 | 0 | 10979.3984 | 6478.3066 | 3927.6584 | 62.0273 | 3622.2625 | 7042.0711 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 6444.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5901 | 1264.1978 | 810.8873 | 459.8054 | 1951.8599 | 0 | 0 | 1651.7814 | 3.0307 | 13003.5894 | 0 | 0 | 0 | 29610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29610
| 147 | ASHP | Improved | 1AAABA | 4/29/2025 9:17:06 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4807.696 | -1113.906 | 0 | -1368.584 | -3290.236 | -10403.42 | 1390.797 | 950.243 | 2061.176 | 3707.062 | 0 | -12874.56 | -32400.09 | 19988 | 6 | 2077614 | 76823 | 5731.5627 | 0 | 10979.3984 | 10815.2585 | 3807.812 | 84.1945 | 3431.01 | 6044.5456 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8739.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.4604 | 1445.0613 | 871.2388 | 474.4778 | 1744.6961 | 0 | 0 | 1651.7814 | 3.0307 | 12344.4392 | 0 | 0 | 0 | 33590 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33590
| 148 | ASHP | Improved | 1AAABB | 4/29/2025 9:17:08 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4807.696 | -1113.906 | 0 | -1368.584 | -3290.236 | -10403.42 | 1390.797 | 950.243 | 2061.176 | 3707.062 | 0 | -12874.56 | -21387.9 | 15300 | 0 | 1949453 | 57275 | 5731.5627 | 0 | 10979.3984 | 6862.8766 | 3856.5662 | 53.8396 | 3614.184 | 6991.4056 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 6515.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5116 | 1193.2388 | 764.5221 | 456.6757 | 1885.0647 | 0 | 0 | 1651.7814 | 3.0307 | 12500.7464 | 0 | 0 | 0 | 29670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29670
| 149 | ASHP | Improved | 1AABAA | 4/29/2025 9:17:10 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4595.778 | -1108.99 | 0 | -1368.584 | -2647.677 | -9885.926 | 1291.173 | 828.067 | 2336.019 | 3307.493 | 0 | -11844.21 | -30744.932 | 17729 | 18 | 2133988 | 74458 | 7386.8492 | 0 | 10979.3984 | 10243.7534 | 3886.2045 | 93.3413 | 3438.1021 | 6099.4671 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8470.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5457 | 1446.2217 | 873.0511 | 477.8907 | 1851.9316 | 0 | 0 | 1651.7814 | 3.0307 | 12841.3266 | 0 | 0 | 0 | 32530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32530
| 150 | ASHP | Improved | 1AABAB | 4/29/2025 9:17:11 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4595.778 | -1108.99 | 0 | -1368.584 | -2647.677 | -9885.926 | 1291.173 | 828.067 | 2336.019 | 3307.493 | 0 | -11844.21 | -19646.307 | 14946 | 0 | 2001583 | 55912 | 7386.8492 | 0 | 10979.3984 | 6205.2179 | 3928.5389 | 62.4505 | 3621.4502 | 7046.4704 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 6360.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5628 | 1251.8054 | 774.5085 | 458.5563 | 1960.4981 | 0 | 0 | 1651.7814 | 3.0307 | 13002.2276 | 0 | 0 | 0 | 29330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29330
| 151 | ASHP | Improved | 1AABBA | 4/29/2025 9:17:13 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4757.098 | -1111.448 | 0 | -1368.584 | -2743.786 | -10273.39 | 1361.822 | 918.716 | 2004.662 | 3602.113 | 0 | -12366.99 | -31697.168 | 18591 | 6 | 2066121 | 75712 | 5731.5627 | 0 | 10979.3984 | 10568.0537 | 3802.8666 | 84.7918 | 3430.1465 | 6045.4773 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8613.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.4263 | 1442.8361 | 873.5562 | 471.0307 | 1755.3207 | 0 | 0 | 1651.7814 | 3.0307 | 12337.7976 | 0 | 0 | 0 | 33240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33240
| 152 | ASHP | Improved | 1AABBB | 4/29/2025 9:17:15 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4757.098 | -1111.448 | 0 | -1368.584 | -2743.786 | -10273.39 | 1361.822 | 918.716 | 2004.662 | 3602.113 | 0 | -12366.99 | -20648.053 | 15060 | 0 | 1937223 | 56503 | 5731.5627 | 0 | 10979.3984 | 6593.4636 | 3856.143 | 54.2423 | 3613.3546 | 6994.1359 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 6428.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5389 | 1182.0955 | 774.7815 | 456.4914 | 1893.3309 | 0 | 0 | 1651.7814 | 3.0307 | 12499.4222 | 0 | 0 | 0 | 29390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29390
| 153 | ASHP | Improved | 1ABAAA | 4/29/2025 9:17:17 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4309.447 | -1108.517 | 0 | -1368.584 | -2898.095 | -6715.244 | 1107.69 | 681.33 | 1973.182 | 2791.834 | 0 | -9845.851 | -28799.863 | 15962 | 20 | 2103856 | 72100 | 7386.8492 | 0 | 10979.3984 | 9553.4122 | 3894.2147 | 97.7781 | 3437.7881 | 6118.4637 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8202.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5423 | 1448.5084 | 869.9317 | 477.5358 | 1900.2456 | 0 | 0 | 1651.7814 | 3.0307 | 12844.4426 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 154 | ASHP | Improved | 1ABAAB | 4/29/2025 9:17:19 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4309.447 | -1108.517 | 0 | -1368.584 | -2898.095 | -6715.244 | 1107.69 | 681.33 | 1973.182 | 2791.834 | 0 | -9845.851 | -17410.645 | 14713 | 0 | 1966076 | 53062 | 7386.8492 | 0 | 10979.3984 | 5385.59 | 3946.5594 | 66.5358 | 3621.4195 | 7067.2042 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 6036.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.6072 | 1269.7746 | 808.1057 | 460.1331 | 1991.5664 | 0 | 0 | 1651.7814 | 3.0307 | 12895.2856 | 0 | 0 | 0 | 28450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28450
| 155 | ASHP | Improved | 1ABABA | 4/29/2025 9:17:21 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4495.643 | -1111.085 | 0 | -1368.584 | -3031.79 | -7048.75 | 1175.832 | 774.124 | 1735.96 | 3092.879 | 0 | -10277.06 | -29716.76 | 16445 | 5 | 2036084 | 72887 | 5731.5627 | 0 | 10979.3984 | 9877.948 | 3817.1089 | 88.372 | 3429.5594 | 6061.2111 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5048 | 1445.1569 | 871.6347 | 477.8907 | 1784.8838 | 0 | 0 | 1651.7814 | 3.0307 | 12341.1253 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 156 | ASHP | Improved | 1ABABB | 4/29/2025 9:17:23 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4495.643 | -1111.085 | 0 | -1368.584 | -3031.79 | -7048.75 | 1175.832 | 774.124 | 1735.96 | 3092.879 | 0 | -10277.06 | -18371.85 | 14813 | 0 | 1900137 | 53879 | 5731.5627 | 0 | 10979.3984 | 5745.4534 | 3872.0645 | 57.4539 | 3613.0611 | 7011.9209 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 6129.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5662 | 1198.389 | 762.215 | 455.8122 | 1922.8019 | 0 | 0 | 1651.7814 | 3.0307 | 12450.2447 | 0 | 0 | 0 | 28780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28780
| 157 | ASHP | Improved | 1ABBAA | 4/29/2025 9:17:25 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4243.205 | -1104.798 | 0 | -1368.584 | -2400.513 | -6592.154 | 1079.972 | 649.019 | 1896.283 | 2684.943 | 0 | -9399.036 | -28086.422 | 15390 | 20 | 2092906 | 71098 | 7386.8492 | 0 | 10979.3984 | 9305.9207 | 3894.8051 | 98.9113 | 3437.0577 | 6125.3783 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8088.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5867 | 1444.29 | 870.0989 | 472.7815 | 1901.9998 | 0 | 0 | 1651.7814 | 3.0307 | 12877.5006 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 158 | ASHP | Improved | 1ABBAB | 4/29/2025 9:17:27 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4243.205 | -1104.798 | 0 | -1368.584 | -2400.513 | -6592.154 | 1079.972 | 649.019 | 1896.283 | 2684.943 | 0 | -9399.036 | -16680.305 | 14549 | 0 | 1954512 | 52107 | 7386.8492 | 0 | 10979.3984 | 5121.8426 | 3949.3785 | 67.3174 | 3620.6789 | 7075.0916 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.6038 | 1257.3821 | 772.0511 | 459.0648 | 2000.5425 | 0 | 0 | 1651.7814 | 3.0307 | 12983.3163 | 0 | 0 | 0 | 28140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28140
| 159 | ASHP | Improved | 1ABBBA | 4/29/2025 9:17:29 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4422.426 | -1108.017 | 0 | -1368.584 | -2509.886 | -6912.568 | 1144.307 | 734.823 | 1667.032 | 2965.544 | 0 | -9809.775 | -28999.439 | 15800 | 5 | 2025367 | 71955 | 5731.5627 | 0 | 10979.3984 | 9640.3337 | 3814.5594 | 89.1945 | 3428.7574 | 6066.88 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5287 | 1442.8702 | 873.9863 | 476.7713 | 1793.4538 | 0 | 0 | 1651.7814 | 3.0307 | 12339.3846 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 160 | ASHP | Improved | 1ABBBB | 4/29/2025 9:17:31 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4422.426 | -1108.017 | 0 | -1368.584 | -2509.886 | -6912.568 | 1144.307 | 734.823 | 1667.032 | 2965.544 | 0 | -9809.775 | -17628.789 | 14637 | 0 | 1888205 | 52956 | 5731.5627 | 0 | 10979.3984 | 5476.16 | 3874.1874 | 58.1502 | 3612.3581 | 7018.0506 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 6024.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5696 | 1187.2354 | 772.3071 | 455.3856 | 1931.348 | 0 | 0 | 1651.7814 | 3.0307 | 12391.1423 | 0 | 0 | 0 | 28390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28390
| 161 | ASHP | Improved | 1ACAAA | 4/29/2025 9:17:33 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4114.481 | -1106.279 | 0 | -1368.584 | -2740.485 | -5198.971 | 1001.451 | 596.498 | 1758.965 | 2485.545 | 0 | -8686.34 | -27448.65 | 15219 | 23 | 2083579 | 70181 | 7386.8492 | 0 | 10979.3984 | 9081.0504 | 3903.6686 | 100.959 | 3437.4263 | 6134.9278 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7984.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.4536 | 1445.464 | 867.1126 | 472.5426 | 1923.6654 | 0 | 0 | 1651.7814 | 3.0307 | 12865.1047 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 162 | ASHP | Improved | 1ACAAB | 4/29/2025 9:17:35 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4114.481 | -1106.279 | 0 | -1368.584 | -2740.485 | -5198.971 | 1001.451 | 596.498 | 1758.965 | 2485.545 | 0 | -8686.34 | -15936.815 | 14550 | 0 | 1943226 | 51268 | 7386.8492 | 0 | 10979.3984 | 4852.7436 | 3959.242 | 69.3345 | 3621.184 | 7084.8595 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5832.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5935 | 1272.6961 | 806.6109 | 460.4027 | 2012.2899 | 0 | 0 | 1651.7814 | 3.0307 | 12985.9272 | 0 | 0 | 0 | 27800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27800
| 163 | ASHP | Improved | 1ACABA | 4/29/2025 9:17:37 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4295.404 | -1109.318 | 0 | -1368.584 | -2870.131 | -5462.616 | 1060.205 | 676.467 | 1555.727 | 2751.975 | 0 | -9061.679 | -28326.133 | 15539 | 6 | 2015380 | 70955 | 5731.5627 | 0 | 10979.3984 | 9405.204 | 3821.3956 | 90.8703 | 3429.0646 | 6074.6923 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8072.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5765 | 1445.2456 | 871.9044 | 477.7679 | 1804.3685 | 0 | 0 | 1651.7814 | 3.0307 | 12359.0263 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 164 | ASHP | Improved | 1ACABB | 4/29/2025 9:17:39 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4295.404 | -1109.318 | 0 | -1368.584 | -2870.131 | -5462.616 | 1060.205 | 676.467 | 1555.727 | 2751.975 | 0 | -9061.679 | -16868.174 | 14640 | 0 | 1876203 | 51980 | 5731.5627 | 0 | 10979.3984 | 5194.9211 | 3882.6891 | 59.5529 | 3612.6891 | 7026.467 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5913.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.6072 | 1201.1194 | 760.9624 | 455.9727 | 1942.4572 | 0 | 0 | 1651.7814 | 3.0307 | 12482.4631 | 0 | 0 | 0 | 28020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28020
| 165 | ASHP | Improved | 1ACBAA | 4/29/2025 9:17:41 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4051.932 | -1102.444 | 0 | -1368.584 | -2267.498 | -5103.075 | 974.032 | 569.918 | 1694.583 | 2392.346 | 0 | -8262.652 | -26685.453 | 14701 | 24 | 2070896 | 69377 | 7386.8492 | 0 | 10979.3984 | 8790.3201 | 3905.184 | 102.2901 | 3436.7949 | 6145.9688 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7892.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.4843 | 1444.5152 | 869.8361 | 467.0102 | 1925.6108 | 0 | 0 | 1651.7814 | 3.0307 | 12841.8112 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 166 | ASHP | Improved | 1ACBAB | 4/29/2025 9:17:43 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4051.932 | -1102.444 | 0 | -1368.584 | -2267.498 | -5103.075 | 974.032 | 569.918 | 1694.583 | 2392.346 | 0 | -8262.652 | -15208.337 | 14398 | 0 | 1931631 | 50384 | 7386.8492 | 0 | 10979.3984 | 4582.7436 | 3964.2113 | 70.3276 | 3620.6038 | 7095.7878 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.573 | 1260.2729 | 770.761 | 459.3276 | 2021.464 | 0 | 0 | 1651.7814 | 3.0307 | 12857.0535 | 0 | 0 | 0 | 27440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27440
| 167 | ASHP | Improved | 1ACBBA | 4/29/2025 9:17:44 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4223.139 | -1105.568 | 0 | -1368.584 | -2371.898 | -5352.303 | 1031.065 | 641.732 | 1493.74 | 2636.707 | 0 | -8618.247 | -27625.125 | 14890 | 6 | 2004363 | 70061 | 5731.5627 | 0 | 10979.3984 | 9154.7842 | 3822.4161 | 92.0819 | 3428.3717 | 6082.5626 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7970.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.4161 | 1442.918 | 874.1091 | 474.5085 | 1813.348 | 0 | 0 | 1651.7814 | 3.0307 | 12338.3027 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 168 | ASHP | Improved | 1ACBBB | 4/29/2025 9:17:47 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -4223.139 | -1105.568 | 0 | -1368.584 | -2371.898 | -5352.303 | 1031.065 | 641.732 | 1493.74 | 2636.707 | 0 | -8618.247 | -16125.185 | 14491 | 0 | 1864331 | 51102 | 5731.5627 | 0 | 10979.3984 | 4923.2556 | 3886.0782 | 60.4369 | 3611.9997 | 7034.8254 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5813.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5662 | 1189.9965 | 770.9897 | 454.9283 | 1951.1944 | 0 | 0 | 1651.7814 | 3.0307 | 12481.2379 | 0 | 0 | 0 | 27600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27600
| 169 | ASHP | Improved | 1BAAAA | 4/29/2025 9:17:49 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2686.747 | -1110.092 | 0 | -1368.584 | -2999.972 | -9452.697 | 1203.151 | 729.658 | 2102.148 | 2990.746 | 0 | -10592.39 | -29572.854 | 16466 | 18 | 2114298 | 73262 | 7386.8492 | 0 | 10979.3984 | 9819.7876 | 3884.0816 | 94.3584 | 3438.1396 | 6093.7572 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8334.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5116 | 1448.2593 | 870.017 | 478.9488 | 1850.3104 | 0 | 0 | 1651.7814 | 3.0307 | 12876.2378 | 0 | 0 | 0 | 32150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32150
| 170 | ASHP | Improved | 1BAAAB | 4/29/2025 9:17:50 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2686.747 | -1110.092 | 0 | -1368.584 | -2999.972 | -9452.697 | 1203.151 | 729.658 | 2102.148 | 2990.746 | 0 | -10592.39 | -18293.15 | 14835 | 0 | 1978735 | 54226 | 7386.8492 | 0 | 10979.3984 | 5705.6378 | 3931.6686 | 63.4642 | 3621.5765 | 7041.9243 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 6169.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5219 | 1267.0409 | 809.9317 | 460.0239 | 1949.5425 | 0 | 0 | 1651.7814 | 3.0307 | 12896.5245 | 0 | 0 | 0 | 28790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28790
| 171 | ASHP | Improved | 1BAABA | 4/29/2025 9:17:52 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2787.15 | -1112.567 | 0 | -1368.584 | -3133.969 | -9907.344 | 1276.18 | 828.088 | 1841.14 | 3306.102 | 0 | -11058.11 | -30500.01 | 17091 | 5 | 2046796 | 74029 | 5731.5627 | 0 | 10979.3984 | 10146.7261 | 3806.4775 | 85.3754 | 3430.0168 | 6039.9995 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8421.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5969 | 1445.2968 | 870.8122 | 475.7679 | 1744.2251 | 0 | 0 | 1651.7814 | 3.0307 | 12342.5382 | 0 | 0 | 0 | 32150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32150
| 172 | ASHP | Improved | 1BAABB | 4/29/2025 9:17:54 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2787.15 | -1112.567 | 0 | -1368.584 | -3133.969 | -9907.344 | 1276.18 | 828.088 | 1841.14 | 3306.102 | 0 | -11058.11 | -19282.312 | 14938 | 0 | 1913684 | 54940 | 5731.5627 | 0 | 10979.3984 | 6079.4295 | 3859.0748 | 54.7508 | 3613.3922 | 6989.6649 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 6250.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5901 | 1195.4914 | 764.0545 | 456.3925 | 1882.307 | 0 | 0 | 1651.7814 | 3.0307 | 12485.4563 | 0 | 0 | 0 | 29270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29270
| 173 | ASHP | Improved | 1BABAA | 4/29/2025 9:17:56 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2650.875 | -1106.92 | 0 | -1368.584 | -2489.491 | -9285.394 | 1174.579 | 695.408 | 2021.372 | 2878.022 | 0 | -10131.88 | -28879.422 | 15828 | 17 | 2102970 | 72327 | 7386.8492 | 0 | 10979.3984 | 9573.6579 | 3878.614 | 95.1024 | 3437.2011 | 6097.706 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8228.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5287 | 1446.4163 | 872.488 | 475.3856 | 1852.9179 | 0 | 0 | 1651.7814 | 3.0307 | 12844.4597 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 174 | ASHP | Improved | 1BABAB | 4/29/2025 9:17:58 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2650.875 | -1106.92 | 0 | -1368.584 | -2489.491 | -9285.394 | 1174.579 | 695.408 | 2021.372 | 2878.022 | 0 | -10131.88 | -17559.363 | 14643 | 0 | 1966672 | 53277 | 7386.8492 | 0 | 10979.3984 | 5436.6207 | 3932.5492 | 64.0307 | 3620.7983 | 7046.3646 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 6061.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5833 | 1254.5869 | 773.7576 | 458.8054 | 1958.1773 | 0 | 0 | 1651.7814 | 3.0307 | 12885.4017 | 0 | 0 | 0 | 28450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28450
| 175 | ASHP | Improved | 1BABBA | 4/29/2025 9:18:00 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2750.431 | -1109.786 | 0 | -1368.584 | -2601.236 | -9733.007 | 1244.313 | 789.069 | 1772.734 | 3180.707 | 0 | -10576.22 | -29835.41 | 16310 | 5 | 2036522 | 72979 | 5731.5627 | 0 | 10979.3984 | 9919.7807 | 3805.6891 | 86.1638 | 3429.0987 | 6043.0541 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8302.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.498 | 1443.0545 | 873.0204 | 474.802 | 1752.522 | 0 | 0 | 1651.7814 | 3.0307 | 12340.8659 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 176 | ASHP | Improved | 1BABBB | 4/29/2025 9:18:02 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2750.431 | -1109.786 | 0 | -1368.584 | -2601.236 | -9733.007 | 1244.313 | 789.069 | 1772.734 | 3180.707 | 0 | -10576.22 | -18535.979 | 14750 | 0 | 1901263 | 54068 | 5731.5627 | 0 | 10979.3984 | 5803.2896 | 3859.8768 | 55.2833 | 3612.5594 | 6993.6001 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 6151.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5423 | 1184.3037 | 774.2764 | 455.9795 | 1890.5493 | 0 | 0 | 1651.7814 | 3.0307 | 12480.4324 | 0 | 0 | 0 | 28850 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28850
| 177 | ASHP | Improved | 1BBAAA | 4/29/2025 9:18:04 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2487.478 | -1105.918 | 0 | -1368.584 | -2699.953 | -6244.541 | 988.083 | 567.608 | 1692.615 | 2400.977 | 0 | -8257.193 | -26900.965 | 14779 | 20 | 2073179 | 69516 | 7386.8492 | 0 | 10979.3984 | 8873.3133 | 3899.1703 | 100.2799 | 3437.1738 | 6120.5387 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7908.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.4843 | 1448.6825 | 869.3788 | 471.8907 | 1901.877 | 0 | 0 | 1651.7814 | 3.0307 | 12845.429 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 178 | ASHP | Improved | 1BBAAB | 4/29/2025 9:18:06 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2487.478 | -1105.918 | 0 | -1368.584 | -2699.953 | -6244.541 | 988.083 | 567.608 | 1692.615 | 2400.977 | 0 | -8257.193 | -15332.377 | 14494 | 0 | 1931954 | 50538 | 7386.8492 | 0 | 10979.3984 | 4626.5355 | 3953.8427 | 68.6314 | 3620.9383 | 7070.8151 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5749.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5935 | 1272.6142 | 807.2627 | 460.389 | 1989.4913 | 0 | 0 | 1651.7814 | 3.0307 | 12860.7395 | 0 | 0 | 0 | 27460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27460
| 179 | ASHP | Improved | 1BBABA | 4/29/2025 9:18:08 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2576.924 | -1109.172 | 0 | -1368.584 | -2817.203 | -6532.413 | 1045.754 | 633.641 | 1483.308 | 2629.841 | 0 | -8611.753 | -27723.344 | 15135 | 5 | 2003708 | 70255 | 5731.5627 | 0 | 10979.3984 | 9173.0504 | 3812.184 | 90.2423 | 3428.9622 | 6061.4329 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7992.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.4058 | 1445.3241 | 871.0272 | 477.5119 | 1782.29 | 0 | 0 | 1651.7814 | 3.0307 | 12361.9478 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 180 | ASHP | Improved | 1BBABB | 4/29/2025 9:18:10 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2576.924 | -1109.172 | 0 | -1368.584 | -2817.203 | -6532.413 | 1045.754 | 633.641 | 1483.308 | 2629.841 | 0 | -8611.753 | -16260.664 | 14586 | 0 | 1864995 | 51237 | 5731.5627 | 0 | 10979.3984 | 4968.904 | 3877.5867 | 58.8362 | 3612.457 | 7013.3271 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5901 | 1200.5869 | 761.8156 | 455.9965 | 1920.208 | 0 | 0 | 1651.7814 | 3.0307 | 12484.6031 | 0 | 0 | 0 | 27740 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27740
| 181 | ASHP | Improved | 1BBBAA | 4/29/2025 9:18:12 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2453.632 | -1102.213 | 0 | -1368.584 | -2235.824 | -6131.729 | 961.294 | 543.122 | 1633.018 | 2314.471 | 0 | -7840.077 | -26147.59 | 14499 | 19 | 2060988 | 68691 | 7386.8492 | 0 | 10979.3984 | 8600.1426 | 3896.3205 | 101.6212 | 3436.4741 | 6129.2247 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7814.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5492 | 1444.4675 | 869.546 | 466.4163 | 1903.662 | 0 | 0 | 1651.7814 | 3.0307 | 12844.3266 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 182 | ASHP | Improved | 1BBBAB | 4/29/2025 9:18:14 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2453.632 | -1102.213 | 0 | -1368.584 | -2235.824 | -6131.729 | 961.294 | 543.122 | 1633.018 | 2314.471 | 0 | -7840.077 | -14601.886 | 14331 | 0 | 1919953 | 49690 | 7386.8492 | 0 | 10979.3984 | 4351.1259 | 3957.8051 | 69.5529 | 3620.3751 | 7079.3714 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5799 | 1260.1705 | 771.3037 | 459.314 | 1998.4708 | 0 | 0 | 1651.7814 | 3.0307 | 12678.5826 | 0 | 0 | 0 | 27090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27090
| 183 | ASHP | Improved | 1BBBBA | 4/29/2025 9:18:16 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2537.231 | -1105.255 | 0 | -1368.584 | -2328.202 | -6398.494 | 1015.841 | 601.014 | 1424.397 | 2518.798 | 0 | -8177.714 | -27060.104 | 14657 | 5 | 1993791 | 69423 | 5731.5627 | 0 | 10979.3984 | 8943.7877 | 3816.7574 | 91.2457 | 3428.1396 | 6068.9858 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.4604 | 1443.0647 | 873.3105 | 474.2696 | 1790.8531 | 0 | 0 | 1651.7814 | 3.0307 | 12340.3778 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 184 | ASHP | Improved | 1BBBBB | 4/29/2025 9:18:18 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2537.231 | -1105.255 | 0 | -1368.584 | -2328.202 | -6398.494 | 1015.841 | 601.014 | 1424.397 | 2518.798 | 0 | -8177.714 | -15512.729 | 14425 | 0 | 1853095 | 50388 | 5731.5627 | 0 | 10979.3984 | 4696.1225 | 3881.3341 | 59.8123 | 3611.8086 | 7021.6922 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5732.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.6004 | 1189.4095 | 771.9522 | 454.9624 | 1928.7473 | 0 | 0 | 1651.7814 | 3.0307 | 12355.5894 | 0 | 0 | 0 | 27310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27310
| 185 | ASHP | Improved | 1BCAAA | 4/29/2025 9:18:20 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2379.674 | -1103.608 | 0 | -1368.584 | -2542.453 | -4809.708 | 875.353 | 499.181 | 1514.865 | 2137.203 | 0 | -7177.425 | -25540.918 | 14534 | 23 | 2052189 | 67598 | 7386.8492 | 0 | 10979.3984 | 8385.0368 | 3907.3273 | 103.8464 | 3436.771 | 6138.3067 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7690.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.6004 | 1445.6347 | 866.5904 | 468.7952 | 1926.0613 | 0 | 0 | 1651.7814 | 3.0307 | 12846.9443 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 186 | ASHP | Improved | 1BCAAB | 4/29/2025 9:18:21 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2379.674 | -1103.608 | 0 | -1368.584 | -2542.453 | -4809.708 | 875.353 | 499.181 | 1514.865 | 2137.203 | 0 | -7177.425 | -13872.931 | 14347 | 0 | 1908566 | 48785 | 7386.8492 | 0 | 10979.3984 | 4079.027 | 3968.1191 | 71.7338 | 3620.9212 | 7089.3032 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5550.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.6038 | 1275.5733 | 805.7815 | 460.6587 | 2010.3411 | 0 | 0 | 1651.7814 | 3.0307 | 12838.3368 | 0 | 0 | 0 | 26690 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26690
| 187 | ASHP | Improved | 1BCABA | 4/29/2025 9:18:24 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2466.026 | -1106.774 | 0 | -1368.584 | -2650.19 | -5027.251 | 925.345 | 554.594 | 1328.401 | 2325.755 | 0 | -7484.73 | -26330.773 | 14667 | 5 | 1982371 | 68388 | 5731.5627 | 0 | 10979.3984 | 8675.1631 | 3823.5901 | 93.099 | 3428.5253 | 6078.6753 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7780.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5287 | 1442.9555 | 869.9317 | 475.5597 | 1801.9487 | 0 | 0 | 1651.7814 | 3.0307 | 12370.1696 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 188 | ASHP | Improved | 1BCABB | 4/29/2025 9:18:26 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2466.026 | -1106.774 | 0 | -1368.584 | -2650.19 | -5027.251 | 925.345 | 554.594 | 1328.401 | 2325.755 | 0 | -7484.73 | -14759.702 | 14423 | 0 | 1841420 | 49506 | 5731.5627 | 0 | 10979.3984 | 4419.1498 | 3891.2761 | 61.4198 | 3612.2659 | 7031.2452 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.6004 | 1203.3514 | 760.5597 | 456.157 | 1940.034 | 0 | 0 | 1651.7814 | 3.0307 | 12227.2106 | 0 | 0 | 0 | 26900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26900
| 189 | ASHP | Improved | 1BCBAA | 4/29/2025 9:18:28 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2340.72 | -1099.367 | 0 | -1368.584 | -2093.955 | -4702.761 | 846.968 | 474.036 | 1453.507 | 2047.615 | 0 | -6783.262 | -24770.082 | 14253 | 24 | 2039483 | 66820 | 7386.8492 | 0 | 10979.3984 | 8097.0915 | 3905.2522 | 105.4846 | 3436.2113 | 6149.2691 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7601.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5969 | 1444.6927 | 869.3412 | 468.0409 | 1928.1159 | 0 | 0 | 1651.7814 | 3.0307 | 12887.0262 | 0 | 0 | 0 | 33590 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33590
| 190 | ASHP | Improved | 1BCBAB | 4/29/2025 9:18:30 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2340.72 | -1099.367 | 0 | -1368.584 | -2093.955 | -4702.761 | 846.968 | 474.036 | 1453.507 | 2047.615 | 0 | -6783.262 | -13150.926 | 14187 | 0 | 1897049 | 47918 | 7386.8492 | 0 | 10979.3984 | 3811.2113 | 3972.5696 | 72.9556 | 3620.3956 | 7099.9926 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5451.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.4911 | 1263.1467 | 818.0341 | 459.5836 | 2019.5903 | 0 | 0 | 1651.7814 | 3.0307 | 12838.4256 | 0 | 0 | 0 | 26260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26260
| 191 | ASHP | Improved | 1BCBBA | 4/29/2025 9:18:32 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2426.571 | -1102.708 | 0 | -1368.584 | -2185.182 | -4918.819 | 895.932 | 526.389 | 1277.256 | 2228.199 | 0 | -7074.087 | -25681.953 | 14434 | 6 | 1972285 | 67540 | 5731.5627 | 0 | 10979.3984 | 8442.972 | 3825.2522 | 94.2628 | 3427.7267 | 6088.1906 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7683.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5867 | 1443.1262 | 873.5699 | 471.0546 | 1809.9657 | 0 | 0 | 1651.7814 | 3.0307 | 12341.528 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 192 | ASHP | Improved | 1BCBBB | 4/29/2025 9:18:33 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2426.571 | -1102.708 | 0 | -1368.584 | -2185.182 | -4918.819 | 895.932 | 526.389 | 1277.256 | 2228.199 | 0 | -7074.087 | -14015.079 | 14250 | 0 | 1829418 | 48606 | 5731.5627 | 0 | 10979.3984 | 4142.7812 | 3895.126 | 62.5051 | 3611.6311 | 7040.723 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5529.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.4536 | 1192.2422 | 770.5255 | 455.1467 | 1948.8428 | 0 | 0 | 1651.7814 | 3.0307 | 12333.801 | 0 | 0 | 0 | 26440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26440
| 193 | ASHP | Improved | 1CAAAA | 4/29/2025 9:18:35 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2061.734 | -1109.454 | 0 | -1368.584 | -2933.382 | -9236.546 | 1162.833 | 685.568 | 1996.693 | 2846.548 | 0 | -10018.06 | -28985.201 | 15997 | 18 | 2104892 | 72230 | 7386.8492 | 0 | 10979.3984 | 9618.989 | 3880.9348 | 94.8601 | 3437.6618 | 6091.8903 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8217.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5662 | 1448.3344 | 869.9283 | 478.6655 | 1850.8599 | 0 | 0 | 1651.7814 | 3.0307 | 12846.8215 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 194 | ASHP | Improved | 1CAAAB | 4/29/2025 9:18:37 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2061.734 | -1109.454 | 0 | -1368.584 | -2933.382 | -9236.546 | 1162.833 | 685.568 | 1996.693 | 2846.548 | 0 | -10018.06 | -17575.867 | 14730 | 0 | 1966765 | 53252 | 7386.8492 | 0 | 10979.3984 | 5443.9347 | 3932.1635 | 63.9863 | 3621.2966 | 7041.0233 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 6058.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5765 | 1267.8054 | 809.6996 | 460.0853 | 1948.6244 | 0 | 0 | 1651.7814 | 3.0307 | 12887.8078 | 0 | 0 | 0 | 28450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28450
| 195 | ASHP | Improved | 1CAABA | 4/29/2025 9:18:39 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2132.7 | -1112.068 | 0 | -1368.584 | -3066.541 | -9686.394 | 1232.179 | 778.36 | 1753.213 | 3146.58 | 0 | -10455.95 | -29818.398 | 16428 | 5 | 2035913 | 72944 | 5731.5627 | 0 | 10979.3984 | 9911.9104 | 3804.0748 | 85.8669 | 3429.6789 | 6038.921 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8298.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5014 | 1445.3275 | 870.5392 | 476.6791 | 1743.8872 | 0 | 0 | 1651.7814 | 3.0307 | 12343.2276 | 0 | 0 | 0 | 32020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32020
| 196 | ASHP | Improved | 1CAABB | 4/29/2025 9:18:41 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2132.7 | -1112.068 | 0 | -1368.584 | -3066.541 | -9686.394 | 1232.179 | 778.36 | 1753.213 | 3146.58 | 0 | -10455.95 | -18554.918 | 14836 | 0 | 1901349 | 54049 | 5731.5627 | 0 | 10979.3984 | 5808.8835 | 3860.2761 | 55.0956 | 3613.0611 | 6989.1325 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 6148.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5389 | 1196.0409 | 763.9624 | 456.1774 | 1881.2251 | 0 | 0 | 1651.7814 | 3.0307 | 12394.6577 | 0 | 0 | 0 | 28890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28890
| 197 | ASHP | Improved | 1CABAA | 4/29/2025 9:18:43 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2035.671 | -1105.962 | 0 | -1368.584 | -2432.857 | -9069.122 | 1132.89 | 652.866 | 1919.648 | 2738.887 | 0 | -9567.904 | -28294.375 | 15425 | 17 | 2093856 | 71327 | 7386.8492 | 0 | 10979.3984 | 9372.948 | 3880.4911 | 95.785 | 3436.9144 | 6096.7401 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8114.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.6038 | 1446.4845 | 872.3242 | 474.3378 | 1852.8804 | 0 | 0 | 1651.7814 | 3.0307 | 12845.429 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 198 | ASHP | Improved | 1CABAB | 4/29/2025 9:18:45 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2035.671 | -1105.962 | 0 | -1368.584 | -2432.857 | -9069.122 | 1132.89 | 652.866 | 1919.648 | 2738.887 | 0 | -9567.904 | -16840.23 | 14566 | 0 | 1954611 | 52447 | 7386.8492 | 0 | 10979.3984 | 5170.648 | 3934.1498 | 64.6212 | 3620.556 | 7046.4977 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5966.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.6004 | 1255.3412 | 773.5528 | 458.8737 | 1957.2626 | 0 | 0 | 1651.7814 | 3.0307 | 12985.7122 | 0 | 0 | 0 | 28130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28130
| 199 | ASHP | Improved | 1CABBA | 4/29/2025 9:18:47 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2106.267 | -1109.082 | 0 | -1368.584 | -2542.893 | -9507.826 | 1201.892 | 739.842 | 1685.911 | 3022.081 | 0 | -9984.928 | -29162.879 | 15696 | 5 | 2026028 | 71893 | 5731.5627 | 0 | 10979.3984 | 9689.0094 | 3807.4707 | 86.6792 | 3428.8154 | 6042.2384 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 8178.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5457 | 1443.0681 | 872.7951 | 475.6109 | 1751.6859 | 0 | 0 | 1651.7814 | 3.0307 | 12352.5587 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 200 | ASHP | Improved | 1CABBB | 4/29/2025 9:18:49 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -2106.267 | -1109.082 | 0 | -1368.584 | -2542.893 | -9507.826 | 1201.892 | 739.842 | 1685.911 | 3022.081 | 0 | -9984.928 | -17806.285 | 14657 | 0 | 1889136 | 53140 | 5731.5627 | 0 | 10979.3984 | 5536.9142 | 3861.1806 | 55.6655 | 3612.2898 | 6993.2554 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 6045.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.6038 | 1184.8497 | 774.2661 | 455.7508 | 1889.4708 | 0 | 0 | 1651.7814 | 3.0307 | 12383.3676 | 0 | 0 | 0 | 28500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28500
| 201 | ASHP | Improved | 1CBAAA | 4/29/2025 9:18:51 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1919.807 | -1105.069 | 0 | -1368.584 | -2635.786 | -6090.363 | 944.852 | 536.355 | 1614.435 | 2288.108 | 0 | -7735.858 | -26202.66 | 14698 | 21 | 2061663 | 68651 | 7386.8492 | 0 | 10979.3984 | 8621.3815 | 3897.9178 | 101.2048 | 3436.9383 | 6121.1394 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7810.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5594 | 1448.7678 | 869.2832 | 469.1843 | 1901.4162 | 0 | 0 | 1651.7814 | 3.0307 | 12846.6986 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 202 | ASHP | Improved | 1CBAAB | 4/29/2025 9:18:52 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1919.807 | -1105.069 | 0 | -1368.584 | -2635.786 | -6090.363 | 944.852 | 536.355 | 1614.435 | 2288.108 | 0 | -7735.858 | -14620.1 | 14425 | 0 | 1919802 | 49715 | 7386.8492 | 0 | 10979.3984 | 4356.9519 | 3956.3444 | 69.3618 | 3620.8291 | 7071.4465 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5655.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5799 | 1273.3651 | 807.0682 | 460.4607 | 1988.6415 | 0 | 0 | 1651.7814 | 3.0307 | 12674.0877 | 0 | 0 | 0 | 27090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27090
| 203 | ASHP | Improved | 1CBABA | 4/29/2025 9:18:54 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1980.672 | -1108.276 | 0 | -1368.584 | -2743.472 | -6354.567 | 999.919 | 592.936 | 1407.051 | 2487.569 | 0 | -8068.097 | -27090.082 | 14777 | 5 | 1993742 | 69361 | 5731.5627 | 0 | 10979.3984 | 8946.9754 | 3819.2352 | 90.8566 | 3428.6414 | 6062.119 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7890.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.457 | 1445.3753 | 870.8054 | 476.9897 | 1781.348 | 0 | 0 | 1651.7814 | 3.0307 | 12342.5689 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 204 | ASHP | Improved | 1CBABB | 4/29/2025 9:18:56 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1980.672 | -1108.276 | 0 | -1368.584 | -2743.472 | -6354.567 | 999.919 | 592.936 | 1407.051 | 2487.569 | 0 | -8068.097 | -15532.794 | 14505 | 0 | 1852916 | 50410 | 5731.5627 | 0 | 10979.3984 | 4700.3887 | 3880.283 | 59.4061 | 3612.2318 | 7014.5284 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5734.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.6072 | 1201.1296 | 761.7917 | 456.0443 | 1919.2012 | 0 | 0 | 1651.7814 | 3.0307 | 12357.8249 | 0 | 0 | 0 | 27360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27360
| 205 | ASHP | Improved | 1CBBAA | 4/29/2025 9:18:58 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1890.967 | -1101.033 | 0 | -1368.584 | -2175.514 | -5960.703 | 915.144 | 509.034 | 1549.085 | 2194.663 | 0 | -7328.874 | -25532.385 | 14329 | 19 | 2050990 | 67645 | 7386.8492 | 0 | 10979.3984 | 8381.0915 | 3896.4741 | 102.4403 | 3436.0748 | 6128.9688 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7695.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.6004 | 1444.5187 | 869.3856 | 465.7918 | 1903.8121 | 0 | 0 | 1651.7814 | 3.0307 | 12845.5655 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 206 | ASHP | Improved | 1CBBAB | 4/29/2025 9:19:00 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1890.967 | -1101.033 | 0 | -1368.584 | -2175.514 | -5960.703 | 915.144 | 509.034 | 1549.085 | 2194.663 | 0 | -7328.874 | -13890.587 | 14267 | 0 | 1907891 | 48822 | 7386.8492 | 0 | 10979.3984 | 4083.5901 | 3960.0372 | 70.3754 | 3620.225 | 7080.1018 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5554.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.6038 | 1260.9282 | 771.1672 | 459.3856 | 1997.6483 | 0 | 0 | 1651.7814 | 3.0307 | 12836.859 | 0 | 0 | 0 | 26680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26680
| 207 | ASHP | Improved | 1CBBBA | 4/29/2025 9:19:02 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1953.508 | -1104.263 | 0 | -1368.584 | -2267.42 | -6226.989 | 968.362 | 564.539 | 1355.358 | 2387.511 | 0 | -7644.995 | -26356.328 | 14470 | 5 | 1981592 | 68506 | 5731.5627 | 0 | 10979.3984 | 8675.1495 | 3817.1328 | 91.9966 | 3427.8768 | 6069.8527 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7793.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5321 | 1443.1193 | 873.1535 | 473.1023 | 1790.2285 | 0 | 0 | 1651.7814 | 3.0307 | 12367.8795 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 208 | ASHP | Improved | 1CBBBB | 4/29/2025 9:19:03 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1953.508 | -1104.263 | 0 | -1368.584 | -2267.42 | -6226.989 | 968.362 | 564.539 | 1355.358 | 2387.511 | 0 | -7644.995 | -14784.144 | 14341 | 0 | 1841026 | 49543 | 5731.5627 | 0 | 10979.3984 | 4427.4604 | 3884.0372 | 60.3549 | 3611.6243 | 7023.2315 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5636.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.6004 | 1189.9624 | 771.8907 | 455.0204 | 1927.7678 | 0 | 0 | 1651.7814 | 3.0307 | 12239.9683 | 0 | 0 | 0 | 26910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26910
| 209 | ASHP | Improved | 1CCAAA | 4/29/2025 9:19:05 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1837.453 | -1102.529 | 0 | -1368.584 | -2471.037 | -4668.903 | 834.556 | 468.014 | 1436.369 | 2024.216 | 0 | -6685.35 | -24818.328 | 14298 | 24 | 2040044 | 66850 | 7386.8492 | 0 | 10979.3984 | 8118.2621 | 3906.2864 | 105.0921 | 3436.6925 | 6139.2896 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7605.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5935 | 1445.6825 | 866.4539 | 469.802 | 1926.5118 | 0 | 0 | 1651.7814 | 3.0307 | 12890.4972 | 0 | 0 | 0 | 33590 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33590
| 210 | ASHP | Improved | 1CCAAB | 4/29/2025 9:19:07 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1837.453 | -1102.529 | 0 | -1368.584 | -2471.037 | -4668.903 | 834.556 | 468.014 | 1436.369 | 2024.216 | 0 | -6685.35 | -13169.726 | 14259 | 0 | 1896776 | 47969 | 7386.8492 | 0 | 10979.3984 | 3816.9007 | 3970.515 | 72.6246 | 3620.8154 | 7090.2929 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5457.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.498 | 1276.3651 | 805.5904 | 460.7338 | 2009.5766 | 0 | 0 | 1651.7814 | 3.0307 | 12840.7839 | 0 | 0 | 0 | 26260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26260
| 211 | ASHP | Improved | 1CCABA | 4/29/2025 9:19:09 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1900.69 | -1105.744 | 0 | -1368.584 | -2576.319 | -4880.153 | 882.06 | 518.723 | 1261.226 | 2198.322 | 0 | -6971.159 | -25694.648 | 14453 | 6 | 1972525 | 67521 | 5731.5627 | 0 | 10979.3984 | 8455.6717 | 3826.3239 | 93.8805 | 3428.2181 | 6079.5524 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7681.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5799 | 1445.4879 | 871.1126 | 474.7679 | 1801.8053 | 0 | 0 | 1651.7814 | 3.0307 | 12343.8488 | 0 | 0 | 0 | 32290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32290
| 212 | ASHP | Improved | 1CCABB | 4/29/2025 9:19:11 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1900.69 | -1105.744 | 0 | -1368.584 | -2576.319 | -4880.153 | 882.06 | 518.723 | 1261.226 | 2198.322 | 0 | -6971.159 | -14035.693 | 14343 | 0 | 1829238 | 48644 | 5731.5627 | 0 | 10979.3984 | 4148.416 | 3893.829 | 62.1331 | 3612.126 | 7032.3202 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.4604 | 1203.9248 | 760.4675 | 456.2082 | 1939.0852 | 0 | 0 | 1651.7814 | 3.0307 | 12336.784 | 0 | 0 | 0 | 26500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26500
| 213 | ASHP | Improved | 1CCBAA | 4/29/2025 9:19:13 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1807.496 | -1098.121 | 0 | -1368.584 | -2032.107 | -4558.85 | 806.316 | 444.131 | 1376.565 | 1935.864 | 0 | -6302.284 | -24165.42 | 14093 | 26 | 2030165 | 65418 | 7386.8492 | 0 | 10979.3984 | 7888.6546 | 3913.8051 | 106.5324 | 3431.341 | 6149.1087 | 0 | 0 | 4533.7266 | 26.5495 | 0 | 0 | 0 | 7442.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5389 | 1444.7439 | 869.1569 | 468.4812 | 1928.5971 | 0 | 0 | 1651.7814 | 3.0307 | 12846.0194 | 0 | 0 | 0 | 32570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32570
| 214 | ASHP | Improved | 1CCBAB | 4/29/2025 9:19:14 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1807.496 | -1098.121 | 0 | -1368.584 | -2032.107 | -4558.85 | 806.316 | 444.131 | 1376.565 | 1935.864 | 0 | -6302.284 | -12452.449 | 14117 | 0 | 1885025 | 46730 | 7386.8492 | 0 | 10979.3984 | 3549.6789 | 3974.4229 | 73.9044 | 3615.6823 | 7100.3441 | 0 | 0 | 4533.7266 | 26.5495 | 0 | 0 | 0 | 5316.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2048.9009 | 0 | 2890.952 | 4001.5594 | 1263.9453 | 817.8327 | 459.1297 | 2018.8565 | 0 | 0 | 1651.7814 | 3.0307 | 12428.0536 | 0 | 0 | 0 | 25600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25600
| 215 | ASHP | Improved | 1CCBBA | 4/29/2025 9:19:17 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1870.439 | -1101.627 | 0 | -1368.584 | -2119.507 | -4764.581 | 853.58 | 490.148 | 1209.543 | 2099.54 | 0 | -6571.928 | -24985.08 | 14235 | 5 | 1961070 | 66583 | 5731.5627 | 0 | 10979.3984 | 8194.2724 | 3827.1294 | 95.2526 | 3427.4844 | 6088.921 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 7574.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.6038 | 1441.1705 | 871.9351 | 468.4948 | 1811.0954 | 0 | 0 | 1651.7814 | 3.0307 | 12342.5894 | 0 | 0 | 0 | 33590 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33590
x | 216 | ASHP | Improved | 1CCBBB | 4/29/2025 9:19:18 | 1167990 | 14789094 | 315037.84 | 174922.89 | 55527.85 | 186240.67 | 0 | -1870.439 | -1101.627 | 0 | -1368.584 | -2119.507 | -4764.581 | 853.58 | 490.148 | 1209.543 | 2099.54 | 0 | -6571.928 | -13293.653 | 14186 | 0 | 1817280 | 47794 | 5731.5627 | 0 | 10979.3984 | 3873.556 | 3897.1225 | 63.2969 | 3611.5492 | 7041.6991 | 0 | 0 | 4533.7198 | 26.5495 | 0 | 0 | 0 | 5437.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.1159 | 0 | 2890.952 | 4001.5219 | 1192.8224 | 770.4743 | 455.2082 | 1947.935 | 0 | 0 | 1651.7814 | 3.0307 | 12335.5758 | 0 | 0 | 0 | 26020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26020
x

## Processed
Column1 | File Name | Run ID | Spandrels R (ft2·°F·h/BTU) | Glass R (ft2·°F·h/BTU) | Air Leakage | LPD | ERV | Controls | HVAC System | Solar PV | Electricity kWh | Natural Gas kWh | Total Energy kWh | TEUI kWh/m² | TEDI kWh/m² | GHGI kgCO2/m² | En Saving % | GHG Saving%
x | 1AAAAA | 1 | 5 | 2.8 | Current | Current | None | Current | Current | No | 11827263.0183 | 11604177.1 | 23431440.1183 | 215.9384 | 100.9439 | 38.8484 | 0% | 0%
| 1AAAAB | 2 | 5 | 2.8 | Current | Current | 75% | Current | Current | No | 12188437.9884 | 7677596.2 | 19866034.1884 | 183.0805 | 65.5869 | 32.5388 | 15.22% | 16.24% |  | m²
| 1AAABA | 3 | 5 | 2.8 | Current | 25% | None | Current | Current | No | 11303698.0618 | 11891141.3 | 23194839.3618 | 213.758 | 103.6877 | 38.5306 | 1.01% | 0.818% | Area | 108509.8217
| 1AAABB | 4 | 5 | 2.8 | Current | 25% | 75% | Current | Current | No | 11666316.0317 | 7972383.5 | 19638699.5317 | 180.9855 | 68.3266 | 32.237 | 16.19% | 17.02% | GHGI - Electricity | 0.17 | 2030
| 1AABAA | 5 | 5 | 2.8 | Improved | Current | None | Current | Current | No | 11828447.0182 | 11403970.2 | 23232417.2182 | 214.1043 | 98.9763 | 38.4997 | 0.8494% | 0.8976% | GHGI - Natural Gas | 0.19 | 2030
| 1AABAB | 6 | 5 | 2.8 | Improved | Current | 75% | Current | Current | No | 12189692.9883 | 7470796.8 | 19660489.7883 | 181.1863 | 63.6202 | 32.1786 | 16.09% | 17.17% | Calibrated TEUI | 215.9384 | kWh/m²
| 1AABBA | 7 | 5 | 2.8 | Improved | 25% | None | Current | Current | No | 11303910.0618 | 11684224.7 | 22988134.7618 | 211.853 | 101.693 | 38.1686 | 1.892% | 1.75% | Calibrated GHGI | 38.8484 | kgCO2/m²
| 1AABBB | 8 | 5 | 2.8 | Improved | 25% | 75% | Current | Current | No | 11666718.0317 | 7766375.2 | 19433093.2317 | 179.0906 | 66.3327 | 31.8769 | 17.06% | 17.95%
| 1ABAAA | 9 | 5 | 4 | Current | Current | None | Current | Current | No | 11840697.0172 | 10787908.4 | 22628605.4172 | 208.5397 | 92.9113 | 37.4401 | 3.426% | 3.625%
| 1ABAAB | 10 | 5 | 4 | Current | Current | 75% | Current | Current | No | 12201176.9873 | 6831881 | 19033057.9873 | 175.404 | 57.5606 | 31.0779 | 18.77% | 20%
| 1ABABA | 11 | 5 | 4 | Current | 25% | None | Current | Current | No | 11313475.061 | 11053923.1 | 22367398.161 | 206.1325 | 95.5177 | 37.0799 | 4.541% | 4.552%
| 1ABABB | 12 | 5 | 4 | Current | 25% | 75% | Current | Current | No | 11676213.0309 | 7115885.9 | 18792098.9309 | 173.1834 | 60.1614 | 30.7527 | 19.8% | 20.84%
| 1ABBAA | 13 | 5 | 4 | Improved | Current | None | Current | Current | No | 11843899.017 | 10587906.6 | 22431805.617 | 206.726 | 90.9407 | 37.0949 | 4.266% | 4.513%
| 1ABBAB | 14 | 5 | 4 | Improved | Current | 75% | Current | Current | No | 12204442.987 | 6622093 | 18826535.987 | 173.5008 | 55.5928 | 30.7157 | 19.65% | 20.93%
| 1ABBBA | 15 | 5 | 4 | Improved | 25% | None | Current | Current | No | 11315829.0608 | 10850551.8 | 22166380.8608 | 204.2799 | 93.5131 | 36.7275 | 5.399% | 5.459%
| 1ABBBB | 16 | 5 | 4 | Improved | 25% | 75% | Current | Current | No | 11678725.0307 | 6907445.7 | 18586170.7307 | 171.2856 | 58.1587 | 30.3917 | 20.68% | 21.77%
| 1ACAAA | 17 | 5 | 5.5 | Current | Current | None | Current | Current | No | 11850580.0164 | 10383832.1 | 22234412.1164 | 204.9069 | 88.9258 | 36.7481 | 5.109% | 5.406%
| 1ACAAB | 18 | 5 | 5.5 | Current | Current | 75% | Current | Current | No | 12210641.9865 | 6406679.4 | 18617321.3865 | 171.5727 | 53.5802 | 30.3482 | 20.55% | 21.88%
| 1ACABA | 19 | 5 | 5.5 | Current | 25% | None | Current | Current | No | 11321347.0603 | 10642932 | 21964279.0603 | 202.4174 | 91.4476 | 36.3726 | 6.262% | 6.373%
| 1ACABB | 20 | 5 | 5.5 | Current | 25% | 75% | Current | Current | No | 11683878.0302 | 6689688.1 | 18373566.1302 | 169.3263 | 56.0956 | 30.0185 | 21.59% | 22.73%
| 1ACBAA | 21 | 5 | 5.5 | Improved | Current | None | Current | Current | No | 11855250.016 | 10181164 | 22036414.016 | 203.0822 | 86.9612 | 36.4005 | 5.954% | 6.301%
| 1ACBAB | 22 | 5 | 5.5 | Improved | Current | 75% | Current | Current | No | 12215403.9861 | 6196276.1 | 18411680.0861 | 169.6775 | 51.6187 | 29.9872 | 21.42% | 22.81%
| 1ACBBA | 23 | 5 | 5.5 | Improved | 25% | None | Current | Current | No | 11324809.06 | 10440293.2 | 21765102.26 | 200.5819 | 89.444 | 36.0232 | 7.112% | 7.272%
| 1ACBBB | 24 | 5 | 5.5 | Improved | 25% | 75% | Current | Current | No | 11687454.0299 | 6475446.5 | 18162900.5299 | 167.3849 | 54.0943 | 29.6489 | 22.48% | 23.68%
| 1BAAAA | 25 | 10 | 2.8 | Current | Current | None | Current | Current | No | 11827896.0183 | 11032446.2 | 22860342.2183 | 210.6753 | 95.3042 | 37.8483 | 2.437% | 2.574%
| 1BAAAB | 26 | 10 | 2.8 | Current | Current | 75% | Current | Current | No | 12188284.9884 | 7085120.9 | 19273405.8884 | 177.619 | 59.9494 | 31.5011 | 17.75% | 18.91%
| 1BAABA | 27 | 10 | 2.8 | Current | 25% | None | Current | Current | No | 11302694.0619 | 11305375.7 | 22608069.7619 | 208.3504 | 97.9846 | 37.5033 | 3.514% | 3.462%
| 1BAABB | 28 | 10 | 2.8 | Current | 25% | 75% | Current | Current | No | 11665153.0318 | 7377417.7 | 19042570.7318 | 175.4917 | 62.6255 | 31.1934 | 18.73% | 19.7%
| 1BABAA | 29 | 10 | 2.8 | Improved | Current | None | Current | Current | No | 11829221.0182 | 10831125.9 | 22660346.9182 | 208.8322 | 93.3227 | 37.4978 | 3.291% | 3.476%
| 1BABAB | 30 | 10 | 2.8 | Improved | Current | 75% | Current | Current | No | 12189950.9882 | 6877618.3 | 19067569.2882 | 175.7221 | 57.9699 | 31.1404 | 18.62% | 19.84%
| 1BABBA | 31 | 10 | 2.8 | Improved | 25% | None | Current | Current | No | 11303518.0618 | 11102033.7 | 22405551.7618 | 206.4841 | 95.972 | 37.1486 | 4.378% | 4.375%
| 1BABBB | 32 | 10 | 2.8 | Improved | 25% | 75% | Current | Current | No | 11666149.0317 | 7165871.7 | 18832020.7317 | 173.5513 | 60.6139 | 30.8245 | 19.63% | 20.65%
| 1BBAAA | 33 | 10 | 4 | Current | Current | None | Current | Current | No | 11843882.017 | 10219195.4 | 22063077.417 | 203.3279 | 87.2954 | 36.4493 | 5.84% | 6.175%
| 1BBAAB | 34 | 10 | 4 | Current | Current | 75% | Current | Current | No | 12203733.9871 | 6233692.2 | 18437426.1871 | 169.9148 | 51.9506 | 30.0345 | 21.31% | 22.69%
| 1BBABA | 35 | 10 | 4 | Current | 25% | None | Current | Current | No | 11315082.0608 | 10480434.2 | 21795516.2608 | 200.8622 | 89.8088 | 36.0783 | 6.982% | 7.131%
| 1BBABB | 36 | 10 | 4 | Current | 25% | 75% | Current | Current | No | 11677331.0308 | 6514386.2 | 18191717.2308 | 167.6504 | 54.4565 | 29.7013 | 22.36% | 23.55%
| 1BBBAA | 37 | 10 | 4 | Improved | Current | None | Current | Current | No | 11847414.0167 | 10014945.1 | 21862359.1167 | 201.4782 | 85.3234 | 36.0972 | 6.696% | 7.082%
| 1BBBAB | 38 | 10 | 4 | Improved | Current | 75% | Current | Current | No | 12207715.9868 | 6019479.9 | 18227195.8868 | 167.9774 | 49.9821 | 29.6656 | 22.21% | 23.64%
| 1BBBBA | 39 | 10 | 4 | Improved | 25% | None | Current | Current | No | 11318717.0605 | 10273957.1 | 21592674.1605 | 198.9928 | 87.7911 | 35.7224 | 7.847% | 8.047%
| 1BBBBB | 40 | 10 | 4 | Improved | 25% | 75% | Current | Current | No | 11680923.0305 | 6299207 | 17980130.0305 | 165.7005 | 52.4417 | 29.3301 | 23.26% | 24.5%
| 1BCAAA | 41 | 10 | 5.5 | Current | Current | None | Current | Current | No | 11854763.0161 | 9816437.6 | 21671200.6161 | 199.7165 | 83.3502 | 35.7611 | 7.512% | 7.947%
| 1BCAAB | 42 | 10 | 5.5 | Current | Current | 75% | Current | Current | No | 12214169.9862 | 5805121.1 | 18019291.0862 | 166.0614 | 48.0133 | 29.3004 | 23.1% | 24.58%
| 1BCABA | 43 | 10 | 5.5 | Current | 25% | None | Current | Current | No | 11325075.06 | 10065604.8 | 21390679.86 | 197.1313 | 85.7532 | 35.3676 | 8.709% | 8.96%
| 1BCABB | 44 | 10 | 5.5 | Current | 25% | 75% | Current | Current | No | 11686581.03 | 6076292.6 | 17762873.63 | 163.6983 | 50.4073 | 28.9487 | 24.19% | 25.48%
| 1BCBAA | 45 | 10 | 5.5 | Improved | Current | None | Current | Current | No | 11859379.0157 | 9619951.8 | 21479330.8157 | 197.9483 | 81.4002 | 35.4243 | 8.331% | 8.814%
| 1BCBAB | 46 | 10 | 5.5 | Improved | Current | 75% | Current | Current | No | 12218871.9858 | 5593868.1 | 17812740.0858 | 164.1579 | 46.0679 | 28.9379 | 23.98% | 25.51%
| 1BCBBA | 47 | 10 | 5.5 | Improved | 25% | None | Current | Current | No | 11329175.0597 | 9861032.2 | 21190207.2597 | 195.2838 | 83.7435 | 35.0158 | 9.565% | 9.865%
| 1BCBBB | 48 | 10 | 5.5 | Improved | 25% | 75% | Current | Current | No | 11690789.0297 | 5857275.1 | 17548064.1297 | 161.7187 | 48.4007 | 28.5718 | 25.11% | 26.45%
| 1CAAAA | 49 | 15 | 2.8 | Current | Current | None | Current | Current | No | 11827622.0183 | 10836487.8 | 22664109.8183 | 208.8669 | 93.3625 | 37.5047 | 3.275% | 3.459%
| 1CAAAB | 50 | 15 | 2.8 | Current | Current | 75% | Current | Current | No | 12187754.9884 | 6880929.2 | 19068684.1884 | 175.7323 | 58.0092 | 31.1428 | 18.62% | 19.84%
| 1CAABA | 51 | 15 | 2.8 | Current | 25% | None | Current | Current | No | 11302525.0619 | 11108567.6 | 22411092.6619 | 206.5352 | 96.0175 | 37.1585 | 4.355% | 4.35%
| 1CAABB | 52 | 15 | 2.8 | Current | 25% | 75% | Current | Current | No | 11664716.0318 | 7172317.7 | 18837033.7318 | 173.5975 | 60.6592 | 30.8335 | 19.61% | 20.63%
| 1CABAA | 53 | 15 | 2.8 | Improved | Current | None | Current | Current | No | 11829752.0181 | 10637130.6 | 22466882.6181 | 207.0493 | 91.3767 | 37.159 | 4.117% | 4.349%
| 1CABAB | 54 | 15 | 2.8 | Improved | Current | 75% | Current | Current | No | 12190153.9882 | 6669266 | 18859419.9882 | 173.8038 | 56.0256 | 30.7759 | 19.51% | 20.78%
| 1CABBA | 55 | 15 | 2.8 | Improved | 25% | None | Current | Current | No | 11303836.0618 | 10905723.7 | 22209559.7618 | 204.6779 | 93.9973 | 36.8053 | 5.215% | 5.259%
| 1CABBB | 56 | 15 | 2.8 | Improved | 25% | 75% | Current | Current | No | 11666154.0317 | 6960068.5 | 18626222.5317 | 171.6547 | 58.6404 | 30.4641 | 20.51% | 21.58%
| 1CBAAA | 57 | 15 | 4 | Current | Current | None | Current | Current | No | 11844499.0169 | 10020453.5 | 21864952.5169 | 201.5021 | 85.3711 | 36.1023 | 6.685% | 7.069%
| 1CBAAB | 58 | 15 | 4 | Current | Current | 75% | Current | Current | No | 12204400.987 | 6024285.1 | 18228686.087 | 167.9911 | 50.0292 | 29.6689 | 22.2% | 23.63%
| 1CBABA | 59 | 15 | 4 | Current | 25% | None | Current | Current | No | 11316126.0608 | 10280608.2 | 21596734.2608 | 199.0302 | 87.8434 | 35.73 | 7.83% | 8.027%
| 1CBABB | 60 | 15 | 4 | Current | 25% | 75% | Current | Current | No | 11677995.0307 | 6304100.1 | 17982095.1307 | 165.7186 | 52.4929 | 29.3341 | 23.26% | 24.49%
| 1CBBAA | 61 | 15 | 4 | Improved | Current | None | Current | Current | No | 11848761.0166 | 9821067 | 21669828.0166 | 199.7038 | 83.4013 | 35.7598 | 7.518% | 7.95%
| 1CBBAB | 62 | 15 | 4 | Improved | Current | 75% | Current | Current | No | 12208485.9867 | 5810893.2 | 18019379.1867 | 166.0622 | 48.0634 | 29.3016 | 23.1% | 24.57%
| 1CBBBA | 63 | 15 | 4 | Improved | 25% | None | Current | Current | No | 11319665.0605 | 10072812.6 | 21392477.6605 | 197.1478 | 85.8236 | 35.3717 | 8.702% | 8.949%
| 1CBBBB | 64 | 15 | 4 | Improved | 25% | 75% | Current | Current | No | 11681627.0304 | 6084438 | 17766065.0304 | 163.7277 | 50.4765 | 28.9552 | 24.18% | 25.47%
| 1CCAAA | 65 | 15 | 5.5 | Current | Current | None | Current | Current | No | 11855584.016 | 9625284.4 | 21480868.416 | 197.9624 | 81.4506 | 35.4277 | 8.325% | 8.805%
| 1CCAAB | 66 | 15 | 5.5 | Current | Current | 75% | Current | Current | No | 12214936.9862 | 5598087.3 | 17813024.2862 | 164.1605 | 46.1171 | 28.9391 | 23.98% | 25.51%
| 1CCABA | 67 | 15 | 5.5 | Current | 25% | None | Current | Current | No | 11326194.0599 | 9867361 | 21193555.0599 | 195.3146 | 83.7981 | 35.0222 | 9.551% | 9.849%
| 1CCABB | 68 | 15 | 5.5 | Current | 25% | 75% | Current | Current | No | 11687454.0299 | 5863047.2 | 17550501.2299 | 161.7411 | 48.4542 | 28.5766 | 25.1% | 26.44%
| 1CCBAA | 69 | 15 | 5.5 | Improved | Current | None | Current | Current | No | 11856234.0159 | 9400524.1 | 21256758.1159 | 195.8971 | 79.5074 | 35.0352 | 9.281% | 9.816%
| 1CCBAB | 70 | 15 | 5.5 | Improved | Current | 75% | Current | Current | No | 12215402.9861 | 5359995.5 | 17575398.4861 | 161.9706 | 44.1801 | 28.5229 | 24.99% | 26.58%
| 1CCBBA | 71 | 15 | 5.5 | Improved | 25% | None | Current | Current | No | 11330349.0596 | 9667447.1 | 20997796.1596 | 193.5106 | 81.7918 | 34.6787 | 10.39% | 10.73%
| 1CCBBB | 72 | 15 | 5.5 | Improved | 25% | 75% | Current | Current | No | 11691584.0296 | 5645582.6 | 17337166.6296 | 159.7751 | 46.4526 | 28.2023 | 26.01% | 27.4%
x | 1AAAAA | 72 | 5 | 2.8 | Current | Current | None | Improved | Current | No | 10660237.1152 | 9782303.1 | 20442540.2152 | 188.3935 | 86.9803 | 33.8299 | 12.76% | 12.92%
| 1AAAAB | 72 | 5 | 2.8 | Current | Current | 75% | Improved | Current | No | 10995001.0874 | 6274360.6 | 17269361.6874 | 159.1502 | 54.992 | 28.212 | 26.3% | 27.38%
| 1AAABA | 72 | 5 | 2.8 | Current | 25% | None | Improved | Current | No | 10134728.1588 | 10069355.2 | 20204083.3588 | 186.1959 | 89.724 | 33.5092 | 13.77% | 13.74%
| 1AAABB | 72 | 5 | 2.8 | Current | 25% | 75% | Improved | Current | No | 10469821.131 | 6568122.4 | 17037943.531 | 157.0175 | 57.7317 | 27.9036 | 27.29% | 28.17%
| 1AABAA | 72 | 5 | 2.8 | Improved | Current | None | Improved | Current | No | 10660853.1151 | 9582096.2 | 20242949.3151 | 186.5541 | 85.0128 | 33.4803 | 13.61% | 13.82%
| 1AABAB | 72 | 5 | 2.8 | Improved | Current | 75% | Improved | Current | No | 10996120.0873 | 6066887.3 | 17063007.3873 | 157.2485 | 53.0252 | 27.8505 | 27.18% | 28.31%
| 1AABBA | 72 | 5 | 2.8 | Improved | 25% | None | Improved | Current | No | 10134184.1589 | 9862907.4 | 19997091.5589 | 184.2883 | 87.7294 | 33.1469 | 14.66% | 14.68%
| 1AABBB | 72 | 5 | 2.8 | Improved | 25% | 75% | Improved | Current | No | 10470035.131 | 6362641.5 | 16832676.631 | 155.1258 | 55.7377 | 27.5441 | 28.16% | 29.1%
| 1ABAAA | 72 | 5 | 4 | Current | Current | None | Improved | Current | No | 10672324.1142 | 8965096.8 | 19637420.9142 | 180.9737 | 78.9477 | 32.4179 | 16.19% | 16.55%
| 1ABAAB | 72 | 5 | 4 | Current | Current | 75% | Improved | Current | No | 11008202.0863 | 5428059.4 | 16436261.4863 | 151.4726 | 46.9655 | 26.7508 | 29.85% | 31.14%
| 1ABABA | 72 | 5 | 4 | Current | 25% | None | Improved | Current | No | 10143109.1581 | 9231375.2 | 19374484.3581 | 178.5505 | 81.5542 | 32.0551 | 17.31% | 17.49%
| 1ABABB | 72 | 5 | 4 | Current | 25% | 75% | Improved | Current | No | 10479977.1302 | 5712591.7 | 16192568.8302 | 149.2268 | 49.5665 | 26.4215 | 30.89% | 31.99%
| 1ABBAA | 72 | 5 | 4 | Improved | Current | None | Improved | Current | No | 10675007.114 | 8765475.9 | 19440483.014 | 179.1587 | 76.9771 | 32.0726 | 17.03% | 17.44%
| 1ABBAB | 72 | 5 | 4 | Improved | Current | 75% | Improved | Current | No | 11010967.0861 | 5218154.2 | 16229121.2861 | 149.5636 | 44.9978 | 26.3876 | 30.74% | 32.08%
| 1ABBBA | 72 | 5 | 4 | Improved | 25% | None | Improved | Current | No | 10144736.158 | 9027652.3 | 19172388.458 | 176.688 | 79.5496 | 31.7009 | 18.18% | 18.4%
| 1ABBBB | 72 | 5 | 4 | Improved | 25% | 75% | Improved | Current | No | 10482204.13 | 5504122.2 | 15986326.33 | 147.3261 | 47.5637 | 26.0599 | 31.77% | 32.92%
| 1ACAAA | 72 | 5 | 5.5 | Current | Current | None | Improved | Current | No | 10681454.1134 | 8560581 | 19242035.1134 | 177.3299 | 74.9621 | 31.7239 | 17.88% | 18.34%
| 1ACAAB | 72 | 5 | 5.5 | Current | Current | 75% | Improved | Current | No | 11017349.0856 | 5002389 | 16019738.0856 | 147.634 | 42.9852 | 26.0198 | 31.63% | 33.02%
| 1ACABA | 72 | 5 | 5.5 | Current | 25% | None | Improved | Current | No | 10149898.1576 | 8819768.8 | 18969666.9576 | 174.8198 | 77.4841 | 31.345 | 19.04% | 19.31%
| 1ACABB | 72 | 5 | 5.5 | Current | 25% | 75% | Improved | Current | No | 10487556.1295 | 5285339.1 | 15772895.2295 | 145.3591 | 45.5006 | 25.6852 | 32.68% | 33.88%
| 1ACBAA | 72 | 5 | 5.5 | Improved | Current | None | Improved | Current | No | 10685484.1131 | 8358498.9 | 19043983.0131 | 175.5047 | 72.9975 | 31.3764 | 18.72% | 19.23%
| 1ACBAB | 72 | 5 | 5.5 | Improved | Current | 75% | Improved | Current | No | 11021634.0852 | 4791839.2 | 15813473.2852 | 145.7331 | 41.0238 | 25.6578 | 32.51% | 33.95%
| 1ACBBA | 72 | 5 | 5.5 | Improved | 25% | None | Improved | Current | No | 10152629.1573 | 8617305.8 | 18769934.9573 | 172.9791 | 75.4804 | 30.9948 | 19.89% | 20.22%
| 1ACBBB | 72 | 5 | 5.5 | Improved | 25% | 75% | Improved | Current | No | 10490660.1293 | 5071390.5 | 15562050.6293 | 143.4161 | 43.4992 | 25.3155 | 33.58% | 34.84%
| 1BAAAA | 72 | 10 | 2.8 | Current | Current | None | Improved | Current | No | 10660402.1152 | 9210103.4 | 19870505.5152 | 183.1217 | 81.3405 | 32.8283 | 15.2% | 15.5%
| 1BAAAB | 72 | 10 | 2.8 | Current | Current | 75% | Improved | Current | No | 10995727.0874 | 5681182.1 | 16676909.1874 | 153.6903 | 49.3545 | 27.1745 | 28.83% | 30.05%
| 1BAABA | 72 | 10 | 2.8 | Current | 25% | None | Improved | Current | No | 10133436.1589 | 9483238 | 19616674.1589 | 180.7825 | 84.0211 | 32.4809 | 16.28% | 16.39%
| 1BAABB | 72 | 10 | 2.8 | Current | 25% | 75% | Improved | Current | No | 10469293.131 | 5974797.4 | 16444090.531 | 151.5447 | 52.0305 | 26.8638 | 29.82% | 30.85%
| 1BABAA | 72 | 10 | 2.8 | Improved | Current | None | Improved | Current | No | 10660985.1151 | 9008871 | 19669856.1151 | 181.2726 | 79.3591 | 32.4768 | 16.05% | 16.4%
| 1BABAB | 72 | 10 | 2.8 | Improved | Current | 75% | Improved | Current | No | 10997008.0872 | 5473708.8 | 16470716.8872 | 151.7901 | 47.3749 | 26.8132 | 29.71% | 30.98%
| 1BABBA | 72 | 10 | 2.8 | Improved | 25% | None | Improved | Current | No | 10133507.1589 | 9279866.7 | 19413373.8589 | 178.9089 | 82.0082 | 32.1249 | 17.15% | 17.31%
| 1BABBB | 72 | 10 | 2.8 | Improved | 25% | 75% | Improved | Current | No | 10470059.131 | 5762548.2 | 16232607.331 | 149.5957 | 50.0189 | 26.4934 | 30.72% | 31.8%
| 1BBAAA | 72 | 10 | 4 | Current | Current | None | Improved | Current | No | 10675214.114 | 8395651.3 | 19070865.414 | 175.7524 | 73.3319 | 31.4254 | 18.61% | 19.11%
| 1BBAAB | 72 | 10 | 4 | Current | Current | 75% | Improved | Current | No | 11010966.0861 | 4829636.2 | 15840602.2861 | 145.9831 | 41.3556 | 25.7073 | 32.4% | 33.83%
| 1BBABA | 72 | 10 | 4 | Current | 25% | None | Improved | Current | No | 10143797.1581 | 8657974.2 | 18801771.3581 | 173.2725 | 75.8453 | 31.0521 | 19.76% | 20.07%
| 1BBABB | 72 | 10 | 4 | Current | 25% | 75% | Improved | Current | No | 10481655.13 | 5111033.4 | 15592688.53 | 143.6984 | 43.8616 | 25.3708 | 33.45% | 34.69%
| 1BBBAA | 72 | 10 | 4 | Improved | Current | None | Improved | Current | No | 10677974.1137 | 8192045.6 | 18870019.7137 | 173.9015 | 71.3597 | 31.0732 | 19.47% | 20.01%
| 1BBBAB | 72 | 10 | 4 | Improved | Current | 75% | Improved | Current | No | 11014378.0858 | 4615570.4 | 15629948.4858 | 144.0418 | 39.3871 | 25.3378 | 33.29% | 34.78%
| 1BBBBA | 72 | 10 | 4 | Improved | 25% | None | Improved | Current | No | 10146765.1578 | 8450764.6 | 18597529.7578 | 171.3903 | 73.8273 | 30.694 | 20.63% | 20.99%
| 1BBBBB | 72 | 10 | 4 | Improved | 25% | 75% | Improved | Current | No | 10484708.1298 | 4895180.3 | 15379888.4298 | 141.7373 | 41.8467 | 24.9976 | 34.36% | 35.65%
| 1BCAAA | 72 | 10 | 5.5 | Current | Current | None | Improved | Current | No | 10684864.1132 | 7992981.4 | 18677845.5132 | 172.1305 | 69.3864 | 30.7354 | 20.29% | 20.88%
| 1BCAAB | 72 | 10 | 5.5 | Current | Current | 75% | Improved | Current | No | 11020808.0853 | 4399570.8 | 15420378.8853 | 142.1104 | 37.4182 | 24.9697 | 34.19% | 35.73%
| 1BCABA | 72 | 10 | 5.5 | Current | 25% | None | Improved | Current | No | 10152323.1574 | 8243437.8 | 18395760.9574 | 169.5308 | 71.7897 | 30.3396 | 21.49% | 21.9%
| 1BCABB | 72 | 10 | 5.5 | Current | 25% | 75% | Improved | Current | No | 10490420.1293 | 4672441.7 | 15162861.8293 | 139.7372 | 39.8123 | 24.6165 | 35.29% | 36.63%
| 1BCBAA | 72 | 10 | 5.5 | Improved | Current | None | Improved | Current | No | 10688462.1129 | 7796642.1 | 18485104.2129 | 170.3542 | 67.4362 | 30.3973 | 21.11% | 21.75%
| 1BCBAB | 72 | 10 | 5.5 | Improved | Current | 75% | Improved | Current | No | 11024682.085 | 4189138.2 | 15213820.285 | 140.2068 | 35.4729 | 24.6073 | 35.07% | 36.66%
| 1BCBBA | 72 | 10 | 5.5 | Improved | 25% | None | Improved | Current | No | 10155589.1571 | 8037927.6 | 18193516.7571 | 167.667 | 69.7798 | 29.9849 | 22.35% | 22.82%
| 1BCBBB | 72 | 10 | 5.5 | Improved | 25% | 75% | Improved | Current | No | 10494016.129 | 4453307 | 14947323.129 | 137.7509 | 37.8056 | 24.2385 | 36.21% | 37.61%
| 1CAAAA | 72 | 15 | 2.8 | Current | Current | None | Improved | Current | No | 10659793.1152 | 9013881.3 | 19673674.4152 | 181.3078 | 79.3989 | 32.4837 | 16.04% | 16.38%
| 1CAAAB | 72 | 15 | 2.8 | Current | Current | 75% | Improved | Current | No | 10995452.0874 | 5477664.3 | 16473116.3874 | 151.8122 | 47.4141 | 26.8177 | 29.7% | 30.97%
| 1CAABA | 72 | 15 | 2.8 | Current | 25% | None | Improved | Current | No | 10132920.159 | 9286224.8 | 19419144.959 | 178.9621 | 82.0538 | 32.1351 | 17.12% | 17.28%
| 1CAABB | 72 | 15 | 2.8 | Current | 25% | 75% | Improved | Current | No | 10469094.1311 | 5769170 | 16238264.1311 | 149.6479 | 50.0642 | 26.5035 | 30.7% | 31.78%
| 1CABAA | 72 | 15 | 2.8 | Improved | Current | None | Improved | Current | No | 10661362.1151 | 8813586.5 | 19474948.6151 | 179.4764 | 77.4131 | 32.1355 | 16.89% | 17.28%
| 1CABAB | 72 | 15 | 2.8 | Improved | Current | 75% | Improved | Current | No | 10997347.0872 | 5265122.1 | 16262469.1872 | 149.8709 | 45.4306 | 26.4485 | 30.6% | 31.92%
| 1CABBA | 72 | 15 | 2.8 | Improved | 25% | None | Improved | Current | No | 10133481.1589 | 9082414 | 19215895.1589 | 177.089 | 80.0337 | 31.7792 | 17.99% | 18.2%
| 1CABBB | 72 | 15 | 2.8 | Improved | 25% | 75% | Improved | Current | No | 10470291.131 | 5556715.7 | 16027006.831 | 147.701 | 48.0455 | 26.1334 | 31.6% | 32.73%
| 1CBAAA | 72 | 15 | 4 | Current | Current | None | Improved | Current | No | 10675472.1139 | 8196938.7 | 18872410.8139 | 173.9235 | 71.4076 | 31.0778 | 19.46% | 20%
| 1CBAAB | 72 | 15 | 4 | Current | Current | 75% | Improved | Current | No | 11011607.086 | 4619467.3 | 15631074.386 | 144.0522 | 39.4342 | 25.3403 | 33.29% | 34.77%
| 1CBABA | 72 | 15 | 4 | Current | 25% | None | Improved | Current | No | 10144369.158 | 8457679.4 | 18602048.558 | 171.4319 | 73.8798 | 30.7023 | 20.61% | 20.97%
| 1CBABB | 72 | 15 | 4 | Current | 25% | 75% | Improved | Current | No | 10482420.13 | 4900454.3 | 15382874.43 | 141.7648 | 41.898 | 25.0032 | 34.35% | 35.64%
| 1CBBAA | 72 | 15 | 4 | Improved | Current | None | Improved | Current | No | 10678756.1137 | 7997991.7 | 18676747.8137 | 172.1203 | 69.4375 | 30.7346 | 20.29% | 20.89%
| 1CBBAB | 72 | 15 | 4 | Improved | Current | 75% | Improved | Current | No | 11015084.0857 | 4406192.6 | 15421276.6857 | 142.1187 | 37.4684 | 24.9723 | 34.19% | 35.72%
| 1CBBBA | 72 | 15 | 4 | Improved | 25% | None | Improved | Current | No | 10147061.1578 | 8250557.7 | 18397618.8578 | 169.548 | 71.8598 | 30.3439 | 21.48% | 21.89%
| 1CBBBB | 72 | 15 | 4 | Improved | 25% | 75% | Improved | Current | No | 10485427.1297 | 4680440.6 | 15165867.7297 | 139.7649 | 39.8815 | 24.6227 | 35.28% | 36.62%
| 1CCAAA | 72 | 15 | 5.5 | Current | Current | None | Improved | Current | No | 10685236.1131 | 7801623.1 | 18486859.2131 | 170.3704 | 67.4867 | 30.4009 | 21.1% | 21.74%
| 1CCAAB | 72 | 15 | 5.5 | Current | Current | 75% | Improved | Current | No | 11021309.0852 | 4193474.6 | 15214783.6852 | 140.2157 | 35.5221 | 24.6096 | 35.07% | 36.65%
| 1CCABA | 72 | 15 | 5.5 | Current | 25% | None | Improved | Current | No | 10153044.1573 | 8044490.8 | 18197534.9573 | 167.704 | 69.8343 | 29.9924 | 22.34% | 22.8%
| 1CCABB | 72 | 15 | 5.5 | Current | 25% | 75% | Improved | Current | No | 10491290.1292 | 4459489.3 | 14950779.4292 | 137.7827 | 37.8592 | 24.245 | 36.19% | 37.59%
| 1CCBAA | 72 | 15 | 5.5 | Improved | Current | None | Improved | Current | No | 10683991.1132 | 7595175.3 | 18279166.4132 | 168.4563 | 65.5459 | 30.0375 | 21.99% | 22.68%
| 1CCBAB | 72 | 15 | 5.5 | Improved | Current | 75% | Improved | Current | No | 11020493.0853 | 3973197.2 | 14993690.2853 | 138.1782 | 33.5874 | 24.2226 | 36.01% | 37.65%
| 1CCBBA | 72 | 15 | 5.5 | Improved | 25% | None | Improved | Current | No | 10156071.157 | 7843932.3 | 18000003.457 | 165.8836 | 67.828 | 29.646 | 23.18% | 23.69%
| 1CCBBB | 72 | 15 | 5.5 | Improved | 25% | 75% | Improved | Current | No | 10494565.129 | 4241995.4 | 14736560.529 | 135.8085 | 35.8576 | 23.8693 | 37.11% | 38.56%
x | 1AAAAA | 72 | 5 | 2.8 | Current | Current | None | Improved | ASHP | No | 13744396.8592 | 2526392.5 | 16270789.3592 | 149.9476 | 84.825 | 25.9567 | 30.56% | 33.18%
| 1AAAAB | 72 | 5 | 2.8 | Current | Current | 75% | Improved | ASHP | No | 12909240.9285 | 1888326.4 | 14797567.3285 | 136.3708 | 55.0185 | 23.5311 | 36.85% | 39.43%
| 1AAABA | 72 | 5 | 2.8 | Current | 25% | None | Improved | ASHP | No | 13318036.8946 | 2560790.7 | 15878827.5946 | 146.3354 | 87.4873 | 25.349 | 32.23% | 34.75%
| 1AAABB | 72 | 5 | 2.8 | Current | 25% | 75% | Improved | ASHP | No | 12496479.9628 | 1909158.7 | 14405638.6628 | 132.7588 | 57.752 | 22.9209 | 38.52% | 41%
| 1AABAA | 72 | 5 | 2.8 | Improved | Current | None | Improved | ASHP | No | 13679403.8646 | 2481915.1 | 16161318.9646 | 148.9388 | 83.018 | 25.777 | 31.03% | 33.65%
| 1AABAB | 72 | 5 | 2.8 | Improved | Current | 75% | Improved | ASHP | No | 12830658.9351 | 1863743.7 | 14694402.6351 | 135.42 | 53.0493 | 23.3649 | 37.29% | 39.86%
| 1AABBA | 72 | 5 | 2.8 | Improved | 25% | None | Improved | ASHP | No | 13244351.9007 | 2523726.2 | 15768078.1007 | 145.3148 | 85.5892 | 25.1687 | 32.71% | 35.21%
| 1AABBB | 72 | 5 | 2.8 | Improved | 25% | 75% | Improved | ASHP | No | 12418092.9693 | 1883433.3 | 14301526.2693 | 131.7994 | 55.7542 | 22.753 | 38.96% | 41.43%
| 1ABAAA | 72 | 5 | 4 | Current | Current | None | Improved | ASHP | No | 13486254.8806 | 2403332.5 | 15889587.3806 | 146.4346 | 77.7659 | 25.3368 | 32.19% | 34.78%
| 1ABAAB | 72 | 5 | 4 | Current | Current | 75% | Improved | ASHP | No | 12603050.9539 | 1768753.1 | 14371804.0539 | 132.447 | 47.0125 | 22.842 | 38.66% | 41.2%
| 1ABABA | 72 | 5 | 4 | Current | 25% | None | Improved | ASHP | No | 13051810.9167 | 2429556 | 15481366.9167 | 142.6725 | 80.2417 | 24.7021 | 33.93% | 36.41%
| 1ABABB | 72 | 5 | 4 | Current | 25% | 75% | Improved | ASHP | No | 12180356.989 | 1795972.8 | 13976329.789 | 128.8024 | 49.608 | 22.2274 | 40.35% | 42.78%
| 1ABBAA | 72 | 5 | 4 | Improved | Current | None | Improved | ASHP | No | 13416056.8865 | 2369930.5 | 15785987.3865 | 145.4798 | 75.8394 | 25.1684 | 32.63% | 35.21%
| 1ABBAB | 72 | 5 | 4 | Improved | Current | 75% | Improved | ASHP | No | 12528921.9601 | 1736904 | 14265825.9601 | 131.4704 | 45.0404 | 22.6701 | 39.12% | 41.64%
| 1ABBBA | 72 | 5 | 4 | Improved | 25% | None | Improved | ASHP | No | 12983109.9224 | 2398498 | 15381607.9224 | 141.7531 | 78.3048 | 24.5401 | 34.35% | 36.83%
| 1ABBBB | 72 | 5 | 4 | Improved | 25% | 75% | Improved | ASHP | No | 12103869.9954 | 1765207.8 | 13869077.7954 | 127.814 | 47.6015 | 22.0537 | 40.81% | 43.23%
| 1ACAAA | 72 | 5 | 5.5 | Current | Current | None | Improved | ASHP | No | 13356272.8914 | 2339341.3 | 15695614.1914 | 144.6469 | 74.1173 | 25.0212 | 33.01% | 35.59%
| 1ACAAB | 72 | 5 | 5.5 | Current | Current | 75% | Improved | ASHP | No | 12456566.9661 | 1708922.5 | 14165489.4661 | 130.5457 | 43.0328 | 22.5077 | 39.54% | 42.06%
| 1ACABA | 72 | 5 | 5.5 | Current | 25% | None | Improved | ASHP | No | 12919089.9277 | 2365154.6 | 15284244.5277 | 140.8559 | 76.4867 | 24.3814 | 34.77% | 37.24%
| 1ACABB | 72 | 5 | 5.5 | Current | 25% | 75% | Improved | ASHP | No | 12026932.0018 | 1732655.5 | 13759587.5018 | 126.805 | 45.5477 | 21.8762 | 41.28% | 43.69%
| 1ACBAA | 72 | 5 | 5.5 | Improved | Current | None | Improved | ASHP | No | 13274972.8982 | 2312561.1 | 15587533.9982 | 143.6509 | 72.0565 | 24.8469 | 33.48% | 36.04%
| 1ACBAB | 72 | 5 | 5.5 | Improved | Current | 75% | Improved | ASHP | No | 12382235.9723 | 1679476 | 14061711.9723 | 129.5893 | 41.0658 | 22.3397 | 39.99% | 42.5%
| 1ACBBA | 72 | 5 | 5.5 | Improved | 25% | None | Improved | ASHP | No | 12848473.9336 | 2335356.5 | 15183830.4336 | 139.9305 | 74.5938 | 24.2186 | 35.2% | 37.66%
| 1ACBBB | 72 | 5 | 5.5 | Improved | 25% | 75% | Improved | ASHP | No | 11950833.0081 | 1703384.8 | 13654217.8081 | 125.8339 | 43.5415 | 21.7057 | 41.73% | 44.13%
| 1BAAAA | 72 | 10 | 2.8 | Current | Current | None | Improved | ASHP | No | 13553195.8751 | 2442067.1 | 15995262.9751 | 147.4084 | 79.8531 | 25.5095 | 31.74% | 34.34%
| 1BAAAB | 72 | 10 | 2.8 | Current | Current | 75% | Improved | ASHP | No | 12684200.9472 | 1807546.3 | 14491747.2472 | 133.5524 | 49.3955 | 23.0371 | 38.15% | 40.7%
| 1BAABA | 72 | 10 | 2.8 | Current | 25% | None | Improved | ASHP | No | 13120488.911 | 2467616.7 | 15588105.611 | 143.6562 | 82.3566 | 24.8764 | 33.47% | 35.97%
| 1BAABB | 72 | 10 | 2.8 | Current | 25% | 75% | Improved | ASHP | No | 12267189.9818 | 1831337.9 | 14098527.8818 | 129.9286 | 52.0664 | 22.4254 | 39.83% | 42.27%
| 1BABAA | 72 | 10 | 2.8 | Improved | Current | None | Improved | ASHP | No | 13480577.8811 | 2410921.2 | 15891499.0811 | 146.4522 | 77.9807 | 25.3412 | 32.18% | 34.77%
| 1BABAB | 72 | 10 | 2.8 | Improved | Current | 75% | Improved | ASHP | No | 12606875.9536 | 1775902.3 | 14382778.2536 | 132.5482 | 47.4141 | 22.8605 | 38.62% | 41.15%
| 1BABBA | 72 | 10 | 2.8 | Improved | 25% | None | Improved | ASHP | No | 13054619.9165 | 2432632.5 | 15487252.4165 | 142.7267 | 80.5621 | 24.7119 | 33.9% | 36.39%
| 1BABBB | 72 | 10 | 2.8 | Improved | 25% | 75% | Improved | ASHP | No | 12187580.9884 | 1802272.3 | 13989853.2884 | 128.9271 | 50.0512 | 22.2498 | 40.29% | 42.73%
| 1BBAAA | 72 | 10 | 4 | Current | Current | None | Improved | ASHP | No | 13289598.897 | 2317190.5 | 15606789.397 | 143.8284 | 72.6384 | 24.8779 | 33.39% | 35.96%
| 1BBAAB | 72 | 10 | 4 | Current | Current | 75% | Improved | ASHP | No | 12384312.9721 | 1684603.5 | 14068916.4721 | 129.6557 | 41.4007 | 22.352 | 39.96% | 42.46%
| 1BBABA | 72 | 10 | 4 | Current | 25% | None | Improved | ASHP | No | 12844270.9339 | 2341831.8 | 15186102.7339 | 139.9514 | 74.859 | 24.2234 | 35.19% | 37.65%
| 1BBABB | 72 | 10 | 4 | Current | 25% | 75% | Improved | ASHP | No | 11955086.0077 | 1707897 | 13662983.0077 | 125.9147 | 43.9073 | 21.7203 | 41.69% | 44.09%
| 1BBBAA | 72 | 10 | 4 | Improved | Current | None | Improved | ASHP | No | 13211457.9034 | 2289677.8 | 15501135.7034 | 142.8547 | 70.6042 | 24.7073 | 33.84% | 36.4%
| 1BBBAB | 72 | 10 | 4 | Improved | Current | 75% | Improved | ASHP | No | 12307390.9785 | 1656329 | 13963719.9785 | 128.6862 | 39.4283 | 22.1819 | 40.41% | 42.9%
| 1BBBBA | 72 | 10 | 4 | Improved | 25% | None | Improved | ASHP | No | 12780702.9392 | 2314114 | 15094816.9392 | 139.1101 | 73.0681 | 24.0753 | 35.58% | 38.03%
| 1BBBBB | 72 | 10 | 4 | Improved | 25% | 75% | Improved | ASHP | No | 11878806.0141 | 1679593.2 | 13558399.2141 | 124.9509 | 41.8877 | 21.5512 | 42.14% | 44.52%
| 1BCAAA | 72 | 10 | 5.5 | Current | Current | None | Improved | ASHP | No | 13155056.9081 | 2253257.9 | 15408314.8081 | 141.9993 | 68.966 | 24.5552 | 34.24% | 36.79%
| 1BCAAB | 72 | 10 | 5.5 | Current | Current | 75% | Improved | ASHP | No | 12234396.9845 | 1626179.3 | 13860576.2845 | 127.7357 | 37.4599 | 22.0148 | 40.85% | 43.33%
| 1BCABA | 72 | 10 | 5.5 | Current | 25% | None | Improved | ASHP | No | 12707492.9453 | 2279598.6 | 14987091.5453 | 138.1174 | 71.0988 | 23.9001 | 36.04% | 38.48%
| 1BCABB | 72 | 10 | 5.5 | Current | 25% | 75% | Improved | ASHP | No | 11803970.0203 | 1650176 | 13454146.0203 | 123.9901 | 39.8544 | 21.3825 | 42.58% | 44.96%
| 1BCBAA | 72 | 10 | 5.5 | Improved | Current | None | Improved | ASHP | No | 13073608.9149 | 2227356.7 | 15300965.6149 | 141.01 | 66.8846 | 24.3822 | 34.7% | 37.24%
| 1BCBAB | 72 | 10 | 5.5 | Improved | Current | 75% | Improved | ASHP | No | 12160566.9907 | 1597260.2 | 13757827.1907 | 126.7888 | 35.5103 | 21.8485 | 41.28% | 43.76%
| 1BCBBA | 72 | 10 | 5.5 | Improved | 25% | None | Improved | ASHP | No | 12642842.9506 | 2251324.1 | 14894167.0506 | 137.261 | 69.3468 | 23.7493 | 36.44% | 38.87%
| 1BCBBB | 72 | 10 | 5.5 | Improved | 25% | 75% | Improved | ASHP | No | 11727031.0267 | 1620202.1 | 13347233.1267 | 123.0048 | 37.8437 | 21.2095 | 43.04% | 45.4%
| 1CAAAA | 72 | 15 | 2.8 | Current | Current | None | Improved | ASHP | No | 13492899.8801 | 2407668.9 | 15900568.7801 | 146.5358 | 78.2663 | 25.3548 | 32.14% | 34.73%
| 1CAAAB | 72 | 15 | 2.8 | Current | Current | 75% | Improved | ASHP | No | 12607473.9536 | 1775052.6 | 14382526.5536 | 132.5459 | 47.4586 | 22.86 | 38.62% | 41.16%
| 1CAABA | 72 | 15 | 2.8 | Current | 25% | None | Improved | ASHP | No | 13050712.9168 | 2431460.5 | 15482173.4168 | 142.6799 | 80.5161 | 24.7037 | 33.93% | 36.41%
| 1CAABB | 72 | 15 | 2.8 | Current | 25% | 75% | Improved | ASHP | No | 12188119.9884 | 1801627.7 | 13989747.6884 | 128.9261 | 50.1023 | 22.2495 | 40.29% | 42.73%
| 1CABAA | 72 | 15 | 2.8 | Improved | Current | None | Improved | ASHP | No | 13422152.886 | 2377577.8 | 15799730.686 | 145.6065 | 76.4009 | 25.1913 | 32.57% | 35.15%
| 1CABAB | 72 | 15 | 2.8 | Improved | Current | 75% | Improved | ASHP | No | 12529555.96 | 1748243.1 | 14277799.06 | 131.5807 | 45.4723 | 22.6909 | 39.07% | 41.59%
| 1CABBA | 72 | 15 | 2.8 | Improved | 25% | None | Improved | ASHP | No | 12987354.922 | 2396417.7 | 15383772.622 | 141.7731 | 78.7461 | 24.5431 | 34.35% | 36.82%
| 1CABBB | 72 | 15 | 2.8 | Improved | 25% | 75% | Improved | ASHP | No | 12109846.9949 | 1771331.5 | 13881178.4949 | 127.9255 | 48.0808 | 22.0738 | 40.76% | 43.18%
| 1CBAAA | 72 | 15 | 4 | Current | Current | None | Improved | ASHP | No | 13215793.9031 | 2288359.3 | 15504153.2031 | 142.8825 | 70.7529 | 24.7118 | 33.83% | 36.39%
| 1CBAAB | 72 | 15 | 4 | Current | Current | 75% | Improved | ASHP | No | 12306424.9786 | 1657149.4 | 13963574.3786 | 128.6849 | 39.4774 | 22.1819 | 40.41% | 42.9%
| 1CBABA | 72 | 15 | 4 | Current | 25% | None | Improved | ASHP | No | 12780383.9392 | 2312033.7 | 15092417.6392 | 139.088 | 73.1491 | 24.0711 | 35.59% | 38.04%
| 1CBABB | 72 | 15 | 4 | Current | 25% | 75% | Improved | ASHP | No | 11877654.0142 | 1680325.7 | 13557979.7142 | 124.947 | 41.9419 | 21.5507 | 42.14% | 44.53%
| 1CBBAA | 72 | 15 | 4 | Improved | Current | None | Improved | ASHP | No | 13147368.9088 | 2254840.1 | 15402209.0088 | 141.943 | 68.943 | 24.5459 | 34.27% | 36.82%
| 1CBBAB | 72 | 15 | 4 | Improved | Current | 75% | Improved | ASHP | No | 12230067.9849 | 1627380.6 | 13857448.5849 | 127.7069 | 37.5076 | 22.0101 | 40.86% | 43.34%
| 1CBBBA | 72 | 15 | 4 | Improved | 25% | None | Improved | ASHP | No | 12702498.9457 | 2283524.8 | 14986023.7457 | 138.1075 | 71.1678 | 23.8992 | 36.04% | 38.48%
| 1CBBBB | 72 | 15 | 4 | Improved | 25% | 75% | Improved | ASHP | No | 11801436.0205 | 1651435.9 | 13452871.9205 | 123.9784 | 39.9204 | 21.3807 | 42.59% | 44.96%
| 1CCAAA | 72 | 15 | 5.5 | Current | Current | None | Improved | ASHP | No | 13077216.9146 | 2228323.6 | 15305540.5146 | 141.0521 | 67.0149 | 24.3896 | 34.68% | 37.22%
| 1CCAAB | 72 | 15 | 5.5 | Current | Current | 75% | Improved | ASHP | No | 12158815.9908 | 1598959.6 | 13757775.5908 | 126.7883 | 35.5611 | 21.8487 | 41.28% | 43.76%
| 1CCABA | 72 | 15 | 5.5 | Current | 25% | None | Improved | ASHP | No | 12644378.9505 | 2250708.8 | 14895087.7505 | 137.2695 | 69.3811 | 23.7507 | 36.43% | 38.86%
| 1CCABB | 72 | 15 | 5.5 | Current | 25% | 75% | Improved | ASHP | No | 11725876.0268 | 1621462 | 13347338.0268 | 123.0058 | 37.8994 | 21.2098 | 43.04% | 45.4%
| 1CCBAA | 72 | 15 | 5.5 | Improved | Current | None | Improved | ASHP | No | 13013877.9198 | 2180593.9 | 15194471.8198 | 140.0285 | 65.2519 | 24.2068 | 35.15% | 37.69%
| 1CCBAB | 72 | 15 | 5.5 | Improved | Current | 75% | Improved | ASHP | No | 12083482.9971 | 1557675.9 | 13641158.8971 | 125.7136 | 33.6243 | 21.6584 | 41.78% | 44.25%
| 1CCBBA | 72 | 15 | 5.5 | Improved | 25% | None | Improved | ASHP | No | 12570956.9566 | 2219445.7 | 14790402.6566 | 136.3047 | 67.4651 | 23.5809 | 36.88% | 39.3%
x | 1CCBBB | 72 | 15 | 5.5 | Improved | 25% | 75% | Improved | ASHP | No | 11649227.0331 | 1593128.9 | 13242355.9331 | 122.0383 | 35.8957 | 21.0402 | 43.48% | 45.84%
x | 1AAAAA | 1 | 5 | 2.8 | Current | Current | None | Current | Current | Yes | 11627263.0183 | 11604177.1 | 23231440.1183 | 214.0953 | 100.9439 | 38.535 | 0.8536% | 0.8066%
| 1AAAAB | 2 | 5 | 2.8 | Current | Current | 0.75 | Current | Current | Yes | 11988437.9884 | 7677596.2 | 19666034.1884 | 181.2374 | 65.5869 | 32.2254 | 16.07% | 17.05%
| 1AAABA | 3 | 5 | 2.8 | Current | 0.25 | None | Current | Current | Yes | 11103698.0618 | 11891141.3 | 22994839.3618 | 211.9148 | 103.6877 | 38.2172 | 1.863% | 1.625%
| 1AAABB | 4 | 5 | 2.8 | Current | 0.25 | 0.75 | Current | Current | Yes | 11466316.0317 | 7972383.5 | 19438699.5317 | 179.1423 | 68.3266 | 31.9236 | 17.04% | 17.83%
| 1AABAA | 5 | 5 | 2.8 | Improved | Current | None | Current | Current | Yes | 11628447.0182 | 11403970.2 | 23032417.2182 | 212.2611 | 98.9763 | 38.1863 | 1.703% | 1.704%
| 1AABAB | 6 | 5 | 2.8 | Improved | Current | 0.75 | Current | Current | Yes | 11989692.9883 | 7470796.8 | 19460489.7883 | 179.3431 | 63.6202 | 31.8653 | 16.95% | 17.98%
| 1AABBA | 7 | 5 | 2.8 | Improved | 0.25 | None | Current | Current | Yes | 11103910.0618 | 11684224.7 | 22788134.7618 | 210.0099 | 101.693 | 37.8553 | 2.745% | 2.556%
| 1AABBB | 8 | 5 | 2.8 | Improved | 0.25 | 0.75 | Current | Current | Yes | 11466718.0317 | 7766375.2 | 19233093.2317 | 177.2475 | 66.3327 | 31.5635 | 17.92% | 18.75%
| 1ABAAA | 9 | 5 | 4 | Current | Current | None | Current | Current | Yes | 11640697.0172 | 10787908.4 | 22428605.4172 | 206.6965 | 92.9113 | 37.1268 | 4.28% | 4.432%
| 1ABAAB | 10 | 5 | 4 | Current | Current | 0.75 | Current | Current | Yes | 12001176.9873 | 6831881 | 18833057.9873 | 173.5609 | 57.5606 | 30.7646 | 19.62% | 20.81%
| 1ABABA | 11 | 5 | 4 | Current | 0.25 | None | Current | Current | Yes | 11113475.061 | 11053923.1 | 22167398.161 | 204.2893 | 95.5177 | 36.7666 | 5.395% | 5.359%
| 1ABABB | 12 | 5 | 4 | Current | 0.25 | 0.75 | Current | Current | Yes | 11476213.0309 | 7115885.9 | 18592098.9309 | 171.3402 | 60.1614 | 30.4394 | 20.65% | 21.65%
| 1ABBAA | 13 | 5 | 4 | Improved | Current | None | Current | Current | Yes | 11643899.017 | 10587906.6 | 22231805.617 | 204.8829 | 90.9407 | 36.7816 | 5.12% | 5.32%
| 1ABBAB | 14 | 5 | 4 | Improved | Current | 0.75 | Current | Current | Yes | 12004442.987 | 6622093 | 18626535.987 | 171.6576 | 55.5928 | 30.4023 | 20.51% | 21.74%
| 1ABBBA | 15 | 5 | 4 | Improved | 0.25 | None | Current | Current | Yes | 11115829.0608 | 10850551.8 | 21966380.8608 | 202.4368 | 93.5131 | 36.4142 | 6.253% | 6.266%
| 1ABBBB | 16 | 5 | 4 | Improved | 0.25 | 0.75 | Current | Current | Yes | 11478725.0307 | 6907445.7 | 18386170.7307 | 169.4425 | 58.1587 | 30.0784 | 21.53% | 22.57%
| 1ACAAA | 17 | 5 | 5.5 | Current | Current | None | Current | Current | Yes | 11650580.0164 | 10383832.1 | 22034412.1164 | 203.0638 | 88.9258 | 36.4347 | 5.962% | 6.213%
| 1ACAAB | 18 | 5 | 5.5 | Current | Current | 0.75 | Current | Current | Yes | 12010641.9865 | 6406679.4 | 18417321.3865 | 169.7295 | 53.5802 | 30.0349 | 21.4% | 22.69%
| 1ACABA | 19 | 5 | 5.5 | Current | 0.25 | None | Current | Current | Yes | 11121347.0603 | 10642932 | 21764279.0603 | 200.5743 | 91.4476 | 36.0593 | 7.115% | 7.179%
| 1ACABB | 20 | 5 | 5.5 | Current | 0.25 | 0.75 | Current | Current | Yes | 11483878.0302 | 6689688.1 | 18173566.1302 | 167.4831 | 56.0956 | 29.7051 | 22.44% | 23.54%
| 1ACBAA | 21 | 5 | 5.5 | Improved | Current | None | Current | Current | Yes | 11655250.016 | 10181164 | 21836414.016 | 201.2391 | 86.9612 | 36.0872 | 6.807% | 7.108%
| 1ACBAB | 22 | 5 | 5.5 | Improved | Current | 0.75 | Current | Current | Yes | 12015403.9861 | 6196276.1 | 18211680.0861 | 167.8344 | 51.6187 | 29.6739 | 22.28% | 23.62%
| 1ACBBA | 23 | 5 | 5.5 | Improved | 0.25 | None | Current | Current | Yes | 11124809.06 | 10440293.2 | 21565102.26 | 198.7387 | 89.444 | 35.7099 | 7.965% | 8.079%
| 1ACBBB | 24 | 5 | 5.5 | Improved | 0.25 | 0.75 | Current | Current | Yes | 11487454.0299 | 6475446.5 | 17962900.5299 | 165.5417 | 54.0943 | 29.3356 | 23.34% | 24.49%
| 1BAAAA | 25 | 10 | 2.8 | Current | Current | None | Current | Current | Yes | 11627896.0183 | 11032446.2 | 22660342.2183 | 208.8322 | 95.3042 | 37.5349 | 3.291% | 3.381%
| 1BAAAB | 26 | 10 | 2.8 | Current | Current | 0.75 | Current | Current | Yes | 11988284.9884 | 7085120.9 | 19073405.8884 | 175.7758 | 59.9494 | 31.1878 | 18.6% | 19.72%
| 1BAABA | 27 | 10 | 2.8 | Current | 0.25 | None | Current | Current | Yes | 11102694.0619 | 11305375.7 | 22408069.7619 | 206.5073 | 97.9846 | 37.19 | 4.368% | 4.269%
| 1BAABB | 28 | 10 | 2.8 | Current | 0.25 | 0.75 | Current | Current | Yes | 11465153.0318 | 7377417.7 | 18842570.7318 | 173.6485 | 62.6255 | 30.88 | 19.58% | 20.51%
| 1BABAA | 29 | 10 | 2.8 | Improved | Current | None | Current | Current | Yes | 11629221.0182 | 10831125.9 | 22460346.9182 | 206.9891 | 93.3227 | 37.1845 | 4.144% | 4.283%
| 1BABAB | 30 | 10 | 2.8 | Improved | Current | 0.75 | Current | Current | Yes | 11989950.9882 | 6877618.3 | 18867569.2882 | 173.8789 | 57.9699 | 30.8271 | 19.48% | 20.65%
| 1BABBA | 31 | 10 | 2.8 | Improved | 0.25 | None | Current | Current | Yes | 11103518.0618 | 11102033.7 | 22205551.7618 | 204.6409 | 95.972 | 36.8352 | 5.232% | 5.182%
| 1BABBB | 32 | 10 | 2.8 | Improved | 0.25 | 0.75 | Current | Current | Yes | 11466149.0317 | 7165871.7 | 18632020.7317 | 171.7081 | 60.6139 | 30.5112 | 20.48% | 21.46%
| 1BBAAA | 33 | 10 | 4 | Current | Current | None | Current | Current | Yes | 11643882.017 | 10219195.4 | 21863077.417 | 201.4848 | 87.2954 | 36.136 | 6.693% | 6.982%
| 1BBAAB | 34 | 10 | 4 | Current | Current | 0.75 | Current | Current | Yes | 12003733.9871 | 6233692.2 | 18237426.1871 | 168.0717 | 51.9506 | 29.7211 | 22.17% | 23.49%
| 1BBABA | 35 | 10 | 4 | Current | 0.25 | None | Current | Current | Yes | 11115082.0608 | 10480434.2 | 21595516.2608 | 199.019 | 89.8088 | 35.7649 | 7.835% | 7.937%
| 1BBABB | 36 | 10 | 4 | Current | 0.25 | 0.75 | Current | Current | Yes | 11477331.0308 | 6514386.2 | 17991717.2308 | 165.8073 | 54.4565 | 29.3879 | 23.22% | 24.35%
| 1BBBAA | 37 | 10 | 4 | Improved | Current | None | Current | Current | Yes | 11647414.0167 | 10014945.1 | 21662359.1167 | 199.635 | 85.3234 | 35.7839 | 7.55% | 7.888%
| 1BBBAB | 38 | 10 | 4 | Improved | Current | 0.75 | Current | Current | Yes | 12007715.9868 | 6019479.9 | 18027195.8868 | 166.1342 | 49.9821 | 29.3523 | 23.06% | 24.44%
| 1BBBBA | 39 | 10 | 4 | Improved | 0.25 | None | Current | Current | Yes | 11118717.0605 | 10273957.1 | 21392674.1605 | 197.1497 | 87.7911 | 35.4091 | 8.701% | 8.853%
| 1BBBBB | 40 | 10 | 4 | Improved | 0.25 | 0.75 | Current | Current | Yes | 11480923.0305 | 6299207 | 17780130.0305 | 163.8573 | 52.4417 | 29.0168 | 24.12% | 25.31%
| 1BCAAA | 41 | 10 | 5.5 | Current | Current | None | Current | Current | Yes | 11654763.0161 | 9816437.6 | 21471200.6161 | 197.8733 | 83.3502 | 35.4478 | 8.366% | 8.753%
| 1BCAAB | 42 | 10 | 5.5 | Current | Current | 0.75 | Current | Current | Yes | 12014169.9862 | 5805121.1 | 17819291.0862 | 164.2182 | 48.0133 | 28.9871 | 23.95% | 25.38%
| 1BCABA | 43 | 10 | 5.5 | Current | 0.25 | None | Current | Current | Yes | 11125075.06 | 10065604.8 | 21190679.86 | 195.2881 | 85.7532 | 35.0542 | 9.563% | 9.767%
| 1BCABB | 44 | 10 | 5.5 | Current | 0.25 | 0.75 | Current | Current | Yes | 11486581.03 | 6076292.6 | 17562873.63 | 161.8552 | 50.4073 | 28.6353 | 25.05% | 26.29%
| 1BCBAA | 45 | 10 | 5.5 | Improved | Current | None | Current | Current | Yes | 11659379.0157 | 9619951.8 | 21279330.8157 | 196.1051 | 81.4002 | 35.111 | 9.185% | 9.62%
| 1BCBAB | 46 | 10 | 5.5 | Improved | Current | 0.75 | Current | Current | Yes | 12018871.9858 | 5593868.1 | 17612740.0858 | 162.3147 | 46.0679 | 28.6245 | 24.83% | 26.32%
| 1BCBBA | 47 | 10 | 5.5 | Improved | 0.25 | None | Current | Current | Yes | 11129175.0597 | 9861032.2 | 20990207.2597 | 193.4406 | 83.7435 | 34.7024 | 10.42% | 10.67%
| 1BCBBB | 48 | 10 | 5.5 | Improved | 0.25 | 0.75 | Current | Current | Yes | 11490789.0297 | 5857275.1 | 17348064.1297 | 159.8755 | 48.4007 | 28.2584 | 25.96% | 27.26%
| 1CAAAA | 49 | 15 | 2.8 | Current | Current | None | Current | Current | Yes | 11627622.0183 | 10836487.8 | 22464109.8183 | 207.0237 | 93.3625 | 37.1914 | 4.128% | 4.265%
| 1CAAAB | 50 | 15 | 2.8 | Current | Current | 0.75 | Current | Current | Yes | 11987754.9884 | 6880929.2 | 18868684.1884 | 173.8892 | 58.0092 | 30.8294 | 19.47% | 20.64%
| 1CAABA | 51 | 15 | 2.8 | Current | 0.25 | None | Current | Current | Yes | 11102525.0619 | 11108567.6 | 22211092.6619 | 204.692 | 96.0175 | 36.8451 | 5.208% | 5.157%
| 1CAABB | 52 | 15 | 2.8 | Current | 0.25 | 0.75 | Current | Current | Yes | 11464716.0318 | 7172317.7 | 18637033.7318 | 171.7543 | 60.6592 | 30.5202 | 20.46% | 21.44%
| 1CABAA | 53 | 15 | 2.8 | Improved | Current | None | Current | Current | Yes | 11629752.0181 | 10637130.6 | 22266882.6181 | 205.2061 | 91.3767 | 36.8456 | 4.97% | 5.155%
| 1CABAB | 54 | 15 | 2.8 | Improved | Current | 0.75 | Current | Current | Yes | 11990153.9882 | 6669266 | 18659419.9882 | 171.9607 | 56.0256 | 30.4626 | 20.37% | 21.59%
| 1CABBA | 55 | 15 | 2.8 | Improved | 0.25 | None | Current | Current | Yes | 11103836.0618 | 10905723.7 | 22009559.7618 | 202.8347 | 93.9973 | 36.492 | 6.068% | 6.066%
| 1CABBB | 56 | 15 | 2.8 | Improved | 0.25 | 0.75 | Current | Current | Yes | 11466154.0317 | 6960068.5 | 18426222.5317 | 169.8116 | 58.6404 | 30.1508 | 21.36% | 22.39%
| 1CBAAA | 57 | 15 | 4 | Current | Current | None | Current | Current | Yes | 11644499.0169 | 10020453.5 | 21664952.5169 | 199.6589 | 85.3711 | 35.7889 | 7.539% | 7.875%
| 1CBAAB | 58 | 15 | 4 | Current | Current | 0.75 | Current | Current | Yes | 12004400.987 | 6024285.1 | 18028686.087 | 166.148 | 50.0292 | 29.3555 | 23.06% | 24.44%
| 1CBABA | 59 | 15 | 4 | Current | 0.25 | None | Current | Current | Yes | 11116126.0608 | 10280608.2 | 21396734.2608 | 197.1871 | 87.8434 | 35.4167 | 8.684% | 8.834%
| 1CBABB | 60 | 15 | 4 | Current | 0.25 | 0.75 | Current | Current | Yes | 11477995.0307 | 6304100.1 | 17782095.1307 | 163.8754 | 52.4929 | 29.0208 | 24.11% | 25.3%
| 1CBBAA | 61 | 15 | 4 | Improved | Current | None | Current | Current | Yes | 11648761.0166 | 9821067 | 21469828.0166 | 197.8607 | 83.4013 | 35.4465 | 8.372% | 8.757%
| 1CBBAB | 62 | 15 | 4 | Improved | Current | 0.75 | Current | Current | Yes | 12008485.9867 | 5810893.2 | 17819379.1867 | 164.219 | 48.0634 | 28.9883 | 23.95% | 25.38%
| 1CBBBA | 63 | 15 | 4 | Improved | 0.25 | None | Current | Current | Yes | 11119665.0605 | 10072812.6 | 21192477.6605 | 195.3047 | 85.8236 | 35.0584 | 9.555% | 9.756%
| 1CBBBB | 64 | 15 | 4 | Improved | 0.25 | 0.75 | Current | Current | Yes | 11481627.0304 | 6084438 | 17566065.0304 | 161.8846 | 50.4765 | 28.6418 | 25.03% | 26.27%
| 1CCAAA | 65 | 15 | 5.5 | Current | Current | None | Current | Current | Yes | 11655584.016 | 9625284.4 | 21280868.416 | 196.1193 | 81.4506 | 35.1144 | 9.178% | 9.612%
| 1CCAAB | 66 | 15 | 5.5 | Current | Current | 0.75 | Current | Current | Yes | 12014936.9862 | 5598087.3 | 17613024.2862 | 162.3173 | 46.1171 | 28.6258 | 24.83% | 26.31%
| 1CCABA | 67 | 15 | 5.5 | Current | 0.25 | None | Current | Current | Yes | 11126194.0599 | 9867361 | 20993555.0599 | 193.4715 | 83.7981 | 34.7089 | 10.4% | 10.66%
| 1CCABB | 68 | 15 | 5.5 | Current | 0.25 | 0.75 | Current | Current | Yes | 11487454.0299 | 5863047.2 | 17350501.2299 | 159.898 | 48.4542 | 28.2633 | 25.95% | 27.25%
| 1CCBAA | 69 | 15 | 5.5 | Improved | Current | None | Current | Current | Yes | 11656234.0159 | 9400524.1 | 21056758.1159 | 194.0539 | 79.5074 | 34.7218 | 10.13% | 10.62%
| 1CCBAB | 70 | 15 | 5.5 | Improved | Current | 0.75 | Current | Current | Yes | 12015402.9861 | 5359995.5 | 17375398.4861 | 160.1274 | 44.1801 | 28.2096 | 25.85% | 27.39%
| 1CCBBA | 71 | 15 | 5.5 | Improved | 0.25 | None | Current | Current | Yes | 11130349.0596 | 9667447.1 | 20797796.1596 | 191.6674 | 81.7918 | 34.3653 | 11.24% | 11.54%
| 1CCBBB | 72 | 15 | 5.5 | Improved | 0.25 | 0.75 | Current | Current | Yes | 11491584.0296 | 5645582.6 | 17137166.6296 | 157.9319 | 46.4526 | 27.889 | 26.86% | 28.21%
x | 1AAAAA | 72 | 5 | 2.8 | Current | Current | None | Improved | Current | Yes | 10460237.1152 | 9782303.1 | 20242540.2152 | 186.5503 | 86.9803 | 33.5166 | 13.61% | 13.72%
| 1AAAAB | 72 | 5 | 2.8 | Current | Current | 0.75 | Improved | Current | Yes | 10795001.0874 | 6274360.6 | 17069361.6874 | 157.3071 | 54.992 | 27.8987 | 27.15% | 28.19%
| 1AAABA | 72 | 5 | 2.8 | Current | 0.25 | None | Improved | Current | Yes | 9934728.1588 | 10069355.2 | 20004083.3588 | 184.3527 | 89.724 | 33.1959 | 14.63% | 14.55%
| 1AAABB | 72 | 5 | 2.8 | Current | 0.25 | 0.75 | Improved | Current | Yes | 10269821.131 | 6568122.4 | 16837943.531 | 155.1744 | 57.7317 | 27.5902 | 28.14% | 28.98%
| 1AABAA | 72 | 5 | 2.8 | Improved | Current | None | Improved | Current | Yes | 10460853.1151 | 9582096.2 | 20042949.3151 | 184.7109 | 85.0128 | 33.167 | 14.46% | 14.62%
| 1AABAB | 72 | 5 | 2.8 | Improved | Current | 0.75 | Improved | Current | Yes | 10796120.0873 | 6066887.3 | 16863007.3873 | 155.4054 | 53.0252 | 27.5371 | 28.03% | 29.12%
| 1AABBA | 72 | 5 | 2.8 | Improved | 0.25 | None | Improved | Current | Yes | 9934184.1589 | 9862907.4 | 19797091.5589 | 182.4452 | 87.7294 | 32.8336 | 15.51% | 15.48%
| 1AABBB | 72 | 5 | 2.8 | Improved | 0.25 | 0.75 | Improved | Current | Yes | 10270035.131 | 6362641.5 | 16632676.631 | 153.2827 | 55.7377 | 27.2308 | 29.02% | 29.9%
| 1ABAAA | 72 | 5 | 4 | Current | Current | None | Improved | Current | Yes | 10472324.1142 | 8965096.8 | 19437420.9142 | 179.1305 | 78.9477 | 32.1046 | 17.05% | 17.36%
| 1ABAAB | 72 | 5 | 4 | Current | Current | 0.75 | Improved | Current | Yes | 10808202.0863 | 5428059.4 | 16236261.4863 | 149.6294 | 46.9655 | 26.4375 | 30.71% | 31.95%
| 1ABABA | 72 | 5 | 4 | Current | 0.25 | None | Improved | Current | Yes | 9943109.1581 | 9231375.2 | 19174484.3581 | 176.7074 | 81.5542 | 31.7417 | 18.17% | 18.29%
| 1ABABB | 72 | 5 | 4 | Current | 0.25 | 0.75 | Improved | Current | Yes | 10279977.1302 | 5712591.7 | 15992568.8302 | 147.3836 | 49.5665 | 26.1081 | 31.75% | 32.79%
| 1ABBAA | 72 | 5 | 4 | Improved | Current | None | Improved | Current | Yes | 10475007.114 | 8765475.9 | 19240483.014 | 177.3156 | 76.9771 | 31.7593 | 17.89% | 18.25%
| 1ABBAB | 72 | 5 | 4 | Improved | Current | 0.75 | Improved | Current | Yes | 10810967.0861 | 5218154.2 | 16029121.2861 | 147.7205 | 44.9978 | 26.0743 | 31.59% | 32.88%
| 1ABBBA | 72 | 5 | 4 | Improved | 0.25 | None | Improved | Current | Yes | 9944736.158 | 9027652.3 | 18972388.458 | 174.8449 | 79.5496 | 31.3876 | 19.03% | 19.2%
| 1ABBBB | 72 | 5 | 4 | Improved | 0.25 | 0.75 | Improved | Current | Yes | 10282204.13 | 5504122.2 | 15786326.33 | 145.4829 | 47.5637 | 25.7466 | 32.63% | 33.73%
| 1ACAAA | 72 | 5 | 5.5 | Current | Current | None | Improved | Current | Yes | 10481454.1134 | 8560581 | 19042035.1134 | 175.4867 | 74.9621 | 31.4106 | 18.73% | 19.15%
| 1ACAAB | 72 | 5 | 5.5 | Current | Current | 0.75 | Improved | Current | Yes | 10817349.0856 | 5002389 | 15819738.0856 | 145.7908 | 42.9852 | 25.7065 | 32.48% | 33.83%
| 1ACABA | 72 | 5 | 5.5 | Current | 0.25 | None | Improved | Current | Yes | 9949898.1576 | 8819768.8 | 18769666.9576 | 172.9767 | 77.4841 | 31.0316 | 19.9% | 20.12%
| 1ACABB | 72 | 5 | 5.5 | Current | 0.25 | 0.75 | Improved | Current | Yes | 10287556.1295 | 5285339.1 | 15572895.2295 | 143.516 | 45.5006 | 25.3719 | 33.54% | 34.69%
| 1ACBAA | 72 | 5 | 5.5 | Improved | Current | None | Improved | Current | Yes | 10485484.1131 | 8358498.9 | 18843983.0131 | 173.6615 | 72.9975 | 31.0631 | 19.58% | 20.04%
| 1ACBAB | 72 | 5 | 5.5 | Improved | Current | 0.75 | Improved | Current | Yes | 10821634.0852 | 4791839.2 | 15613473.2852 | 143.89 | 41.0238 | 25.3445 | 33.37% | 34.76%
| 1ACBBA | 72 | 5 | 5.5 | Improved | 0.25 | None | Improved | Current | Yes | 9952629.1573 | 8617305.8 | 18569934.9573 | 171.136 | 75.4804 | 30.6814 | 20.75% | 21.02%
| 1ACBBB | 72 | 5 | 5.5 | Improved | 0.25 | 0.75 | Improved | Current | Yes | 10290660.1293 | 5071390.5 | 15362050.6293 | 141.5729 | 43.4992 | 25.0021 | 34.44% | 35.64%
| 1BAAAA | 72 | 10 | 2.8 | Current | Current | None | Improved | Current | Yes | 10460402.1152 | 9210103.4 | 19670505.5152 | 181.2786 | 81.3405 | 32.5149 | 16.05% | 16.3%
| 1BAAAB | 72 | 10 | 2.8 | Current | Current | 0.75 | Improved | Current | Yes | 10795727.0874 | 5681182.1 | 16476909.1874 | 151.8472 | 49.3545 | 26.8611 | 29.68% | 30.86%
| 1BAABA | 72 | 10 | 2.8 | Current | 0.25 | None | Improved | Current | Yes | 9933436.1589 | 9483238 | 19416674.1589 | 178.9393 | 84.0211 | 32.1676 | 17.13% | 17.2%
| 1BAABB | 72 | 10 | 2.8 | Current | 0.25 | 0.75 | Improved | Current | Yes | 10269293.131 | 5974797.4 | 16244090.531 | 149.7016 | 52.0305 | 26.5505 | 30.67% | 31.66%
| 1BABAA | 72 | 10 | 2.8 | Improved | Current | None | Improved | Current | Yes | 10460985.1151 | 9008871 | 19469856.1151 | 179.4294 | 79.3591 | 32.1635 | 16.91% | 17.21%
| 1BABAB | 72 | 10 | 2.8 | Improved | Current | 0.75 | Improved | Current | Yes | 10797008.0872 | 5473708.8 | 16270716.8872 | 149.947 | 47.3749 | 26.4999 | 30.56% | 31.79%
| 1BABBA | 72 | 10 | 2.8 | Improved | 0.25 | None | Improved | Current | Yes | 9933507.1589 | 9279866.7 | 19213373.8589 | 177.0658 | 82.0082 | 31.8116 | 18% | 18.11%
| 1BABBB | 72 | 10 | 2.8 | Improved | 0.25 | 0.75 | Improved | Current | Yes | 10270059.131 | 5762548.2 | 16032607.331 | 147.7526 | 50.0189 | 26.1801 | 31.58% | 32.61%
| 1BBAAA | 72 | 10 | 4 | Current | Current | None | Improved | Current | Yes | 10475214.114 | 8395651.3 | 18870865.414 | 173.9093 | 73.3319 | 31.112 | 19.46% | 19.91%
| 1BBAAB | 72 | 10 | 4 | Current | Current | 0.75 | Improved | Current | Yes | 10810966.0861 | 4829636.2 | 15640602.2861 | 144.14 | 41.3556 | 25.394 | 33.25% | 34.63%
| 1BBABA | 72 | 10 | 4 | Current | 0.25 | None | Improved | Current | Yes | 9943797.1581 | 8657974.2 | 18601771.3581 | 171.4294 | 75.8453 | 30.7388 | 20.61% | 20.87%
| 1BBABB | 72 | 10 | 4 | Current | 0.25 | 0.75 | Improved | Current | Yes | 10281655.13 | 5111033.4 | 15392688.53 | 141.8553 | 43.8616 | 25.0574 | 34.31% | 35.5%
| 1BBBAA | 72 | 10 | 4 | Improved | Current | None | Improved | Current | Yes | 10477974.1137 | 8192045.6 | 18670019.7137 | 172.0583 | 71.3597 | 30.7598 | 20.32% | 20.82%
| 1BBBAB | 72 | 10 | 4 | Improved | Current | 0.75 | Improved | Current | Yes | 10814378.0858 | 4615570.4 | 15429948.4858 | 142.1986 | 39.3871 | 25.0245 | 34.15% | 35.58%
| 1BBBBA | 72 | 10 | 4 | Improved | 0.25 | None | Improved | Current | Yes | 9946765.1578 | 8450764.6 | 18397529.7578 | 169.5471 | 73.8273 | 30.3806 | 21.48% | 21.8%
| 1BBBBB | 72 | 10 | 4 | Improved | 0.25 | 0.75 | Improved | Current | Yes | 10284708.1298 | 4895180.3 | 15179888.4298 | 139.8941 | 41.8467 | 24.6843 | 35.22% | 36.46%
| 1BCAAA | 72 | 10 | 5.5 | Current | Current | None | Improved | Current | Yes | 10484864.1132 | 7992981.4 | 18477845.5132 | 170.2873 | 69.3864 | 30.4221 | 21.14% | 21.69%
| 1BCAAB | 72 | 10 | 5.5 | Current | Current | 0.75 | Improved | Current | Yes | 10820808.0853 | 4399570.8 | 15220378.8853 | 140.2673 | 37.4182 | 24.6563 | 35.04% | 36.53%
| 1BCABA | 72 | 10 | 5.5 | Current | 0.25 | None | Improved | Current | Yes | 9952323.1574 | 8243437.8 | 18195760.9574 | 167.6877 | 71.7897 | 30.0263 | 22.34% | 22.71%
| 1BCABB | 72 | 10 | 5.5 | Current | 0.25 | 0.75 | Improved | Current | Yes | 10290420.1293 | 4672441.7 | 14962861.8293 | 137.8941 | 39.8123 | 24.3032 | 36.14% | 37.44%
| 1BCBAA | 72 | 10 | 5.5 | Improved | Current | None | Improved | Current | Yes | 10488462.1129 | 7796642.1 | 18285104.2129 | 168.5111 | 67.4362 | 30.0839 | 21.96% | 22.56%
| 1BCBAB | 72 | 10 | 5.5 | Improved | Current | 0.75 | Improved | Current | Yes | 10824682.085 | 4189138.2 | 15013820.285 | 138.3637 | 35.4729 | 24.294 | 35.92% | 37.46%
| 1BCBBA | 72 | 10 | 5.5 | Improved | 0.25 | None | Improved | Current | Yes | 9955589.1571 | 8037927.6 | 17993516.7571 | 165.8239 | 69.7798 | 29.6716 | 23.21% | 23.62%
| 1BCBBB | 72 | 10 | 5.5 | Improved | 0.25 | 0.75 | Improved | Current | Yes | 10294016.129 | 4453307 | 14747323.129 | 135.9077 | 37.8056 | 23.9251 | 37.06% | 38.41%
| 1CAAAA | 72 | 15 | 2.8 | Current | Current | None | Improved | Current | Yes | 10459793.1152 | 9013881.3 | 19473674.4152 | 179.4646 | 79.3989 | 32.1704 | 16.89% | 17.19%
| 1CAAAB | 72 | 15 | 2.8 | Current | Current | 0.75 | Improved | Current | Yes | 10795452.0874 | 5477664.3 | 16273116.3874 | 149.9691 | 47.4141 | 26.5044 | 30.55% | 31.77%
| 1CAABA | 72 | 15 | 2.8 | Current | 0.25 | None | Improved | Current | Yes | 9932920.159 | 9286224.8 | 19219144.959 | 177.1189 | 82.0538 | 31.8218 | 17.98% | 18.09%
| 1CAABB | 72 | 15 | 2.8 | Current | 0.25 | 0.75 | Improved | Current | Yes | 10269094.1311 | 5769170 | 16038264.1311 | 147.8047 | 50.0642 | 26.1901 | 31.55% | 32.58%
| 1CABAA | 72 | 15 | 2.8 | Improved | Current | None | Improved | Current | Yes | 10461362.1151 | 8813586.5 | 19274948.6151 | 177.6332 | 77.4131 | 31.8221 | 17.74% | 18.09%
| 1CABAB | 72 | 15 | 2.8 | Improved | Current | 0.75 | Improved | Current | Yes | 10797347.0872 | 5265122.1 | 16062469.1872 | 148.0278 | 45.4306 | 26.1352 | 31.45% | 32.73%
| 1CABBA | 72 | 15 | 2.8 | Improved | 0.25 | None | Improved | Current | Yes | 9933481.1589 | 9082414 | 19015895.1589 | 175.2458 | 80.0337 | 31.4658 | 18.84% | 19%
| 1CABBB | 72 | 15 | 2.8 | Improved | 0.25 | 0.75 | Improved | Current | Yes | 10270291.131 | 5556715.7 | 15827006.831 | 145.8578 | 48.0455 | 25.82 | 32.45% | 33.54%
| 1CBAAA | 72 | 15 | 4 | Current | Current | None | Improved | Current | Yes | 10475472.1139 | 8196938.7 | 18672410.8139 | 172.0804 | 71.4076 | 30.7645 | 20.31% | 20.81%
| 1CBAAB | 72 | 15 | 4 | Current | Current | 0.75 | Improved | Current | Yes | 10811607.086 | 4619467.3 | 15431074.386 | 142.209 | 39.4342 | 25.027 | 34.14% | 35.58%
| 1CBABA | 72 | 15 | 4 | Current | 0.25 | None | Improved | Current | Yes | 9944369.158 | 8457679.4 | 18402048.558 | 169.5888 | 73.8798 | 30.389 | 21.46% | 21.78%
| 1CBABB | 72 | 15 | 4 | Current | 0.25 | 0.75 | Improved | Current | Yes | 10282420.13 | 4900454.3 | 15182874.43 | 139.9217 | 41.898 | 24.6899 | 35.2% | 36.45%
| 1CBBAA | 72 | 15 | 4 | Improved | Current | None | Improved | Current | Yes | 10478756.1137 | 7997991.7 | 18476747.8137 | 170.2772 | 69.4375 | 30.4213 | 21.15% | 21.69%
| 1CBBAB | 72 | 15 | 4 | Improved | Current | 0.75 | Improved | Current | Yes | 10815084.0857 | 4406192.6 | 15221276.6857 | 140.2756 | 37.4684 | 24.659 | 35.04% | 36.53%
| 1CBBBA | 72 | 15 | 4 | Improved | 0.25 | None | Improved | Current | Yes | 9947061.1578 | 8250557.7 | 18197618.8578 | 167.7048 | 71.8598 | 30.0305 | 22.34% | 22.7%
| 1CBBBB | 72 | 15 | 4 | Improved | 0.25 | 0.75 | Improved | Current | Yes | 10285427.1297 | 4680440.6 | 14965867.7297 | 137.9218 | 39.8815 | 24.3094 | 36.13% | 37.42%
| 1CCAAA | 72 | 15 | 5.5 | Current | Current | None | Improved | Current | Yes | 10485236.1131 | 7801623.1 | 18286859.2131 | 168.5272 | 67.4867 | 30.0876 | 21.96% | 22.55%
| 1CCAAB | 72 | 15 | 5.5 | Current | Current | 0.75 | Improved | Current | Yes | 10821309.0852 | 4193474.6 | 15014783.6852 | 138.3726 | 35.5221 | 24.2963 | 35.92% | 37.46%
| 1CCABA | 72 | 15 | 5.5 | Current | 0.25 | None | Improved | Current | Yes | 9953044.1573 | 8044490.8 | 17997534.9573 | 165.8609 | 69.8343 | 29.6791 | 23.19% | 23.6%
| 1CCABB | 72 | 15 | 5.5 | Current | 0.25 | 0.75 | Improved | Current | Yes | 10291290.1292 | 4459489.3 | 14750779.4292 | 135.9396 | 37.8592 | 23.9317 | 37.05% | 38.4%
| 1CCBAA | 72 | 15 | 5.5 | Improved | Current | None | Improved | Current | Yes | 10483991.1132 | 7595175.3 | 18079166.4132 | 166.6132 | 65.5459 | 29.7241 | 22.84% | 23.49%
| 1CCBAB | 72 | 15 | 5.5 | Improved | Current | 0.75 | Improved | Current | Yes | 10820493.0853 | 3973197.2 | 14793690.2853 | 136.335 | 33.5874 | 23.9093 | 36.86% | 38.45%
| 1CCBBA | 72 | 15 | 5.5 | Improved | 0.25 | None | Improved | Current | Yes | 9956071.157 | 7843932.3 | 17800003.457 | 164.0405 | 67.828 | 29.3326 | 24.03% | 24.49%
| 1CCBBB | 72 | 15 | 5.5 | Improved | 0.25 | 0.75 | Improved | Current | Yes | 10294565.129 | 4241995.4 | 14536560.529 | 133.9654 | 35.8576 | 23.556 | 37.96% | 39.36%
x | 1AAAAA | 72 | 5 | 2.8 | Current | Current | None | Improved | ASHP | Yes | 13544396.8592 | 2526392.5 | 16070789.3592 | 148.1045 | 84.825 | 25.6434 | 31.41% | 33.99%
| 1AAAAB | 72 | 5 | 2.8 | Current | Current | 0.75 | Improved | ASHP | Yes | 12709240.9285 | 1888326.4 | 14597567.3285 | 134.5276 | 55.0185 | 23.2177 | 37.7% | 40.23%
| 1AAABA | 72 | 5 | 2.8 | Current | 0.25 | None | Improved | ASHP | Yes | 13118036.8946 | 2560790.7 | 15678827.5946 | 144.4922 | 87.4873 | 25.0357 | 33.09% | 35.56%
| 1AAABB | 72 | 5 | 2.8 | Current | 0.25 | 0.75 | Improved | ASHP | Yes | 12296479.9628 | 1909158.7 | 14205638.6628 | 130.9157 | 57.752 | 22.6076 | 39.37% | 41.81%
| 1AABAA | 72 | 5 | 2.8 | Improved | Current | None | Improved | ASHP | Yes | 13479403.8646 | 2481915.1 | 15961318.9646 | 147.0956 | 83.018 | 25.4637 | 31.88% | 34.45%
| 1AABAB | 72 | 5 | 2.8 | Improved | Current | 0.75 | Improved | ASHP | Yes | 12630658.9351 | 1863743.7 | 14494402.6351 | 133.5769 | 53.0493 | 23.0516 | 38.14% | 40.66%
| 1AABBA | 72 | 5 | 2.8 | Improved | 0.25 | None | Improved | ASHP | Yes | 13044351.9007 | 2523726.2 | 15568078.1007 | 143.4716 | 85.5892 | 24.8553 | 33.56% | 36.02%
| 1AABBB | 72 | 5 | 2.8 | Improved | 0.25 | 0.75 | Improved | ASHP | Yes | 12218092.9693 | 1883433.3 | 14101526.2693 | 129.9562 | 55.7542 | 22.4397 | 39.82% | 42.24%
| 1ABAAA | 72 | 5 | 4 | Current | Current | None | Improved | ASHP | Yes | 13286254.8806 | 2403332.5 | 15689587.3806 | 144.5914 | 77.7659 | 25.0235 | 33.04% | 35.59%
| 1ABAAB | 72 | 5 | 4 | Current | Current | 0.75 | Improved | ASHP | Yes | 12403050.9539 | 1768753.1 | 14171804.0539 | 130.6039 | 47.0125 | 22.5287 | 39.52% | 42.01%
| 1ABABA | 72 | 5 | 4 | Current | 0.25 | None | Improved | ASHP | Yes | 12851810.9167 | 2429556 | 15281366.9167 | 140.8293 | 80.2417 | 24.3888 | 34.78% | 37.22%
| 1ABABB | 72 | 5 | 4 | Current | 0.25 | 0.75 | Improved | ASHP | Yes | 11980356.989 | 1795972.8 | 13776329.789 | 126.9593 | 49.608 | 21.9141 | 41.21% | 43.59%
| 1ABBAA | 72 | 5 | 4 | Improved | Current | None | Improved | ASHP | Yes | 13216056.8865 | 2369930.5 | 15585987.3865 | 143.6367 | 75.8394 | 24.855 | 33.48% | 36.02%
| 1ABBAB | 72 | 5 | 4 | Improved | Current | 0.75 | Improved | ASHP | Yes | 12328921.9601 | 1736904 | 14065825.9601 | 129.6272 | 45.0404 | 22.3568 | 39.97% | 42.45%
| 1ABBBA | 72 | 5 | 4 | Improved | 0.25 | None | Improved | ASHP | Yes | 12783109.9224 | 2398498 | 15181607.9224 | 139.91 | 78.3048 | 24.2268 | 35.21% | 37.64%
| 1ABBBB | 72 | 5 | 4 | Improved | 0.25 | 0.75 | Improved | ASHP | Yes | 11903869.9954 | 1765207.8 | 13669077.7954 | 125.9709 | 47.6015 | 21.7404 | 41.66% | 44.04%
| 1ACAAA | 72 | 5 | 5.5 | Current | Current | None | Improved | ASHP | Yes | 13156272.8914 | 2339341.3 | 15495614.1914 | 142.8038 | 74.1173 | 24.7078 | 33.87% | 36.4%
| 1ACAAB | 72 | 5 | 5.5 | Current | Current | 0.75 | Improved | ASHP | Yes | 12256566.9661 | 1708922.5 | 13965489.4661 | 128.7025 | 43.0328 | 22.1944 | 40.4% | 42.87%
| 1ACABA | 72 | 5 | 5.5 | Current | 0.25 | None | Improved | ASHP | Yes | 12719089.9277 | 2365154.6 | 15084244.5277 | 139.0127 | 76.4867 | 24.0681 | 35.62% | 38.05%
| 1ACABB | 72 | 5 | 5.5 | Current | 0.25 | 0.75 | Improved | ASHP | Yes | 11826932.0018 | 1732655.5 | 13559587.5018 | 124.9618 | 45.5477 | 21.5629 | 42.13% | 44.49%
| 1ACBAA | 72 | 5 | 5.5 | Improved | Current | None | Improved | ASHP | Yes | 13074972.8982 | 2312561.1 | 15387533.9982 | 141.8078 | 72.0565 | 24.5336 | 34.33% | 36.85%
| 1ACBAB | 72 | 5 | 5.5 | Improved | Current | 0.75 | Improved | ASHP | Yes | 12182235.9723 | 1679476 | 13861711.9723 | 127.7462 | 41.0658 | 22.0264 | 40.84% | 43.3%
| 1ACBBA | 72 | 5 | 5.5 | Improved | 0.25 | None | Improved | ASHP | Yes | 12648473.9336 | 2335356.5 | 14983830.4336 | 138.0873 | 74.5938 | 23.9053 | 36.05% | 38.47%
| 1ACBBB | 72 | 5 | 5.5 | Improved | 0.25 | 0.75 | Improved | ASHP | Yes | 11750833.0081 | 1703384.8 | 13454217.8081 | 123.9908 | 43.5415 | 21.3924 | 42.58% | 44.93%
| 1BAAAA | 72 | 10 | 2.8 | Current | Current | None | Improved | ASHP | Yes | 13353195.8751 | 2442067.1 | 15795262.9751 | 145.5653 | 79.8531 | 25.1962 | 32.59% | 35.14%
| 1BAAAB | 72 | 10 | 2.8 | Current | Current | 0.75 | Improved | ASHP | Yes | 12484200.9472 | 1807546.3 | 14291747.2472 | 131.7093 | 49.3955 | 22.7237 | 39.01% | 41.51%
| 1BAABA | 72 | 10 | 2.8 | Current | 0.25 | None | Improved | ASHP | Yes | 12920488.911 | 2467616.7 | 15388105.611 | 141.813 | 82.3566 | 24.563 | 34.33% | 36.77%
| 1BAABB | 72 | 10 | 2.8 | Current | 0.25 | 0.75 | Improved | ASHP | Yes | 12067189.9818 | 1831337.9 | 13898527.8818 | 128.0854 | 52.0664 | 22.1121 | 40.68% | 43.08%
| 1BABAA | 72 | 10 | 2.8 | Improved | Current | None | Improved | ASHP | Yes | 13280577.8811 | 2410921.2 | 15691499.0811 | 144.609 | 77.9807 | 25.0279 | 33.03% | 35.58%
| 1BABAB | 72 | 10 | 2.8 | Improved | Current | 0.75 | Improved | ASHP | Yes | 12406875.9536 | 1775902.3 | 14182778.2536 | 130.705 | 47.4141 | 22.5472 | 39.47% | 41.96%
| 1BABBA | 72 | 10 | 2.8 | Improved | 0.25 | None | Improved | ASHP | Yes | 12854619.9165 | 2432632.5 | 15287252.4165 | 140.8836 | 80.5621 | 24.3986 | 34.76% | 37.2%
| 1BABBB | 72 | 10 | 2.8 | Improved | 0.25 | 0.75 | Improved | ASHP | Yes | 11987580.9884 | 1802272.3 | 13789853.2884 | 127.0839 | 50.0512 | 21.9365 | 41.15% | 43.53%
| 1BBAAA | 72 | 10 | 4 | Current | Current | None | Improved | ASHP | Yes | 13089598.897 | 2317190.5 | 15406789.397 | 141.9852 | 72.6384 | 24.5646 | 34.25% | 36.77%
| 1BBAAB | 72 | 10 | 4 | Current | Current | 0.75 | Improved | ASHP | Yes | 12184312.9721 | 1684603.5 | 13868916.4721 | 127.8125 | 41.4007 | 22.0386 | 40.81% | 43.27%
| 1BBABA | 72 | 10 | 4 | Current | 0.25 | None | Improved | ASHP | Yes | 12644270.9339 | 2341831.8 | 14986102.7339 | 138.1083 | 74.859 | 23.91 | 36.04% | 38.45%
| 1BBABB | 72 | 10 | 4 | Current | 0.25 | 0.75 | Improved | ASHP | Yes | 11755086.0077 | 1707897 | 13462983.0077 | 124.0716 | 43.9073 | 21.407 | 42.54% | 44.9%
| 1BBBAA | 72 | 10 | 4 | Improved | Current | None | Improved | ASHP | Yes | 13011457.9034 | 2289677.8 | 15301135.7034 | 141.0115 | 70.6042 | 24.394 | 34.7% | 37.21%
| 1BBBAB | 72 | 10 | 4 | Improved | Current | 0.75 | Improved | ASHP | Yes | 12107390.9785 | 1656329 | 13763719.9785 | 126.8431 | 39.4283 | 21.8686 | 41.26% | 43.71%
| 1BBBBA | 72 | 10 | 4 | Improved | 0.25 | None | Improved | ASHP | Yes | 12580702.9392 | 2314114 | 14894816.9392 | 137.267 | 73.0681 | 23.7619 | 36.43% | 38.83%
| 1BBBBB | 72 | 10 | 4 | Improved | 0.25 | 0.75 | Improved | ASHP | Yes | 11678806.0141 | 1679593.2 | 13358399.2141 | 123.1077 | 41.8877 | 21.2379 | 42.99% | 45.33%
| 1BCAAA | 72 | 10 | 5.5 | Current | Current | None | Improved | ASHP | Yes | 12955056.9081 | 2253257.9 | 15208314.8081 | 140.1561 | 68.966 | 24.2418 | 35.09% | 37.6%
| 1BCAAB | 72 | 10 | 5.5 | Current | Current | 0.75 | Improved | ASHP | Yes | 12034396.9845 | 1626179.3 | 13660576.2845 | 125.8925 | 37.4599 | 21.7015 | 41.7% | 44.14%
| 1BCABA | 72 | 10 | 5.5 | Current | 0.25 | None | Improved | ASHP | Yes | 12507492.9453 | 2279598.6 | 14787091.5453 | 136.2742 | 71.0988 | 23.5868 | 36.89% | 39.28%
| 1BCABB | 72 | 10 | 5.5 | Current | 0.25 | 0.75 | Improved | ASHP | Yes | 11603970.0203 | 1650176 | 13254146.0203 | 122.147 | 39.8544 | 21.0691 | 43.43% | 45.77%
| 1BCBAA | 72 | 10 | 5.5 | Improved | Current | None | Improved | ASHP | Yes | 12873608.9149 | 2227356.7 | 15100965.6149 | 139.1668 | 66.8846 | 24.0689 | 35.55% | 38.04%
| 1BCBAB | 72 | 10 | 5.5 | Improved | Current | 0.75 | Improved | ASHP | Yes | 11960566.9907 | 1597260.2 | 13557827.1907 | 124.9456 | 35.5103 | 21.5352 | 42.14% | 44.57%
| 1BCBBA | 72 | 10 | 5.5 | Improved | 0.25 | None | Improved | ASHP | Yes | 12442842.9506 | 2251324.1 | 14694167.0506 | 135.4179 | 69.3468 | 23.436 | 37.29% | 39.67%
| 1BCBBB | 72 | 10 | 5.5 | Improved | 0.25 | 0.75 | Improved | ASHP | Yes | 11527031.0267 | 1620202.1 | 13147233.1267 | 121.1617 | 37.8437 | 20.8961 | 43.89% | 46.21%
| 1CAAAA | 72 | 15 | 2.8 | Current | Current | None | Improved | ASHP | Yes | 13292899.8801 | 2407668.9 | 15700568.7801 | 144.6926 | 78.2663 | 25.0415 | 32.99% | 35.54%
| 1CAAAB | 72 | 15 | 2.8 | Current | Current | 0.75 | Improved | ASHP | Yes | 12407473.9536 | 1775052.6 | 14182526.5536 | 130.7027 | 47.4586 | 22.5466 | 39.47% | 41.96%
| 1CAABA | 72 | 15 | 2.8 | Current | 0.25 | None | Improved | ASHP | Yes | 12850712.9168 | 2431460.5 | 15282173.4168 | 140.8368 | 80.5161 | 24.3904 | 34.78% | 37.22%
| 1CAABB | 72 | 15 | 2.8 | Current | 0.25 | 0.75 | Improved | ASHP | Yes | 11988119.9884 | 1801627.7 | 13789747.6884 | 127.0829 | 50.1023 | 21.9362 | 41.15% | 43.53%
| 1CABAA | 72 | 15 | 2.8 | Improved | Current | None | Improved | ASHP | Yes | 13222152.886 | 2377577.8 | 15599730.686 | 143.7633 | 76.4009 | 24.878 | 33.42% | 35.96%
| 1CABAB | 72 | 15 | 2.8 | Improved | Current | 0.75 | Improved | ASHP | Yes | 12329555.96 | 1748243.1 | 14077799.06 | 129.7376 | 45.4723 | 22.3776 | 39.92% | 42.4%
| 1CABBA | 72 | 15 | 2.8 | Improved | 0.25 | None | Improved | ASHP | Yes | 12787354.922 | 2396417.7 | 15183772.622 | 139.9299 | 78.7461 | 24.2298 | 35.2% | 37.63%
| 1CABBB | 72 | 15 | 2.8 | Improved | 0.25 | 0.75 | Improved | ASHP | Yes | 11909846.9949 | 1771331.5 | 13681178.4949 | 126.0824 | 48.0808 | 21.7605 | 41.61% | 43.99%
| 1CBAAA | 72 | 15 | 4 | Current | Current | None | Improved | ASHP | Yes | 13015793.9031 | 2288359.3 | 15304153.2031 | 141.0393 | 70.7529 | 24.3985 | 34.69% | 37.2%
| 1CBAAB | 72 | 15 | 4 | Current | Current | 0.75 | Improved | ASHP | Yes | 12106424.9786 | 1657149.4 | 13763574.3786 | 126.8417 | 39.4774 | 21.8685 | 41.26% | 43.71%
| 1CBABA | 72 | 15 | 4 | Current | 0.25 | None | Improved | ASHP | Yes | 12580383.9392 | 2312033.7 | 14892417.6392 | 137.2449 | 73.1491 | 23.7578 | 36.44% | 38.84%
| 1CBABB | 72 | 15 | 4 | Current | 0.25 | 0.75 | Improved | ASHP | Yes | 11677654.0142 | 1680325.7 | 13357979.7142 | 123.1039 | 41.9419 | 21.2374 | 42.99% | 45.33%
| 1CBBAA | 72 | 15 | 4 | Improved | Current | None | Improved | ASHP | Yes | 12947368.9088 | 2254840.1 | 15202209.0088 | 140.0998 | 68.943 | 24.2326 | 35.12% | 37.62%
| 1CBBAB | 72 | 15 | 4 | Improved | Current | 0.75 | Improved | ASHP | Yes | 12030067.9849 | 1627380.6 | 13657448.5849 | 125.8637 | 37.5076 | 21.6968 | 41.71% | 44.15%
| 1CBBBA | 72 | 15 | 4 | Improved | 0.25 | None | Improved | ASHP | Yes | 12502498.9457 | 2283524.8 | 14786023.7457 | 136.2644 | 71.1678 | 23.5858 | 36.9% | 39.29%
| 1CBBBB | 72 | 15 | 4 | Improved | 0.25 | 0.75 | Improved | ASHP | Yes | 11601436.0205 | 1651435.9 | 13252871.9205 | 122.1352 | 39.9204 | 21.0674 | 43.44% | 45.77%
| 1CCAAA | 72 | 15 | 5.5 | Current | Current | None | Improved | ASHP | Yes | 12877216.9146 | 2228323.6 | 15105540.5146 | 139.209 | 67.0149 | 24.0762 | 35.53% | 38.03%
| 1CCAAB | 72 | 15 | 5.5 | Current | Current | 0.75 | Improved | ASHP | Yes | 11958815.9908 | 1598959.6 | 13557775.5908 | 124.9451 | 35.5611 | 21.5354 | 42.14% | 44.57%
| 1CCABA | 72 | 15 | 5.5 | Current | 0.25 | None | Improved | ASHP | Yes | 12444378.9505 | 2250708.8 | 14695087.7505 | 135.4263 | 69.3811 | 23.4373 | 37.28% | 39.67%
| 1CCABB | 72 | 15 | 5.5 | Current | 0.25 | 0.75 | Improved | ASHP | Yes | 11525876.0268 | 1621462 | 13147338.0268 | 121.1627 | 37.8994 | 20.8965 | 43.89% | 46.21%
| 1CCBAA | 72 | 15 | 5.5 | Improved | Current | None | Improved | ASHP | Yes | 12813877.9198 | 2180593.9 | 14994471.8198 | 138.1854 | 65.2519 | 23.8934 | 36.01% | 38.5%
| 1CCBAB | 72 | 15 | 5.5 | Improved | Current | 0.75 | Improved | ASHP | Yes | 11883482.9971 | 1557675.9 | 13441158.8971 | 123.8704 | 33.6243 | 21.3451 | 42.64% | 45.06%
| 1CCBBA | 72 | 15 | 5.5 | Improved | 0.25 | None | Improved | ASHP | Yes | 12370956.9566 | 2219445.7 | 14590402.6566 | 134.4616 | 67.4651 | 23.2675 | 37.73% | 40.11%
x | 1CCBBB | 72 | 15 | 5.5 | Improved | 0.25 | 0.75 | Improved | ASHP | Yes | 11449227.0331 | 1593128.9 | 13042355.9331 | 120.1952 | 35.8957 | 20.7268 | 44.34% | 46.65%
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Measures
0 | 1 | 2 | 3 | 4 | 5 | 6
| Parameter | Spandrels | Glass | Air Leakage | LPD Drop | ERV
| A | 5 | 2.8 | Current | Current | None
| B | 10 | 4 | Improved | 25% | 75%
| C | 15 | 5.5